45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 15.88
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 3.52
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 9.41
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 9.41
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 9.41
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 15.88
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 3.52
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2020 | 13.2507
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2025 | 13.0667
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2025 | 22.0556
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2025 | 4.8889
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2030 | 12.8877
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2040 | 12.7135
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2050 | 12.544
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2050 | 21.1733
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2050 | 4.6933
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2020 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2025 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | lower | 2025 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | upper | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2030 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2040 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2050 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | lower | 2050 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | upper | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2025 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2025 | 1
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2050 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2050 | 1
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2020 | 1.71
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2025 | 1.72
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2025 | 1.72
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2025 | 1.72
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2030 | 1.73
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2040 | 1.74
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2050 | 1.75
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2050 | 1.75
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2050 | 1.75
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2020 | 0.048566
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2025 | 0.048774
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2025 | 0.027614
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2025 | 0.069033
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2030 | 0.048978
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2040 | 0.049177
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2050 | 0.049374
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2050 | 0.027614
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2050 | 0.069033
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2020 | 4.5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2025 | 4.5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2025 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2025 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2030 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2040 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2050 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2050 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2050 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2020 | 0.02
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2025 | 0.02
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2025 | 0.01
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2025 | 0.03
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2030 | 0.02
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2040 | 0.02
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2050 | 0.02
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2050 | 0.01
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2050 | 0.03
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 17.5844
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 17.5094
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 29.84
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 6.62
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 17.4366
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 17.3657
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 17.2967
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 29.84
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 6.62
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2020 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2025 | 1
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2025 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2030 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2040 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2050 | 1
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2050 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2025 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2025 | 7
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2050 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2050 | 7
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2020 | 25
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2025 | 25
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2025 | 25
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2025 | 30
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2030 | 30
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2040 | 30
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2050 | 30
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2050 | 25
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2050 | 35
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2020 | 2.9286
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2025 | 2.953
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2025 | 3.1686
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2025 | 2.7479
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2030 | 2.9773
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2040 | 3.0015
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2050 | 3.0257
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2050 | 3.2946
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2050 | 2.8422
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 1.4795
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 1.4359
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 0.81838
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 2.1064
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 1.3924
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 1.3489
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 1.3054
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 0.74398
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 1.9149
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2020 | 0.12197
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2025 | 0.11838
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2025 | 0.15855
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2025 | 0.035733
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2030 | 0.1148
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2040 | 0.11121
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2050 | 0.10762
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2050 | 0.14413
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2050 | 0.032485
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 0.49315
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 0.47865
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 0.28106
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 0.7234
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 0.46414
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 0.44964
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 0.43513
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 0.25551
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 0.65763
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2025 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2025 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2025 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2040 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2050 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2050 | 0
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2020 | 2.993
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2025 | 2.9566
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2025 | 2.9301
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2025 | 2.93
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2030 | 2.9196
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2040 | 2.8599
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2050 | 2.7994
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2050 | 2.7407
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2050 | 2.7407
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2020 | 17300
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2025 | 16800
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2025 | 16800
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2025 | 16800
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2030 | 16300
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2040 | 15800
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2050 | 15300
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2050 | 15300
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2050 | 15300
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.0946
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2025 | 2.033
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2025 | 1.258
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2025 | 2.8655
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2030 | 1.9714
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2040 | 1.9098
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2050 | 1.8482
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2050 | 1.1436
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2050 | 2.605
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2020 | 2.993
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2025 | 2.9566
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2025 | 2.9301
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2025 | 2.93
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2030 | 2.9196
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2040 | 2.8599
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2050 | 2.7994
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2050 | 2.7407
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2050 | 2.7407
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2020 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2030 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2040 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2020 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2025 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2025 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2025 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2030 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2040 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2050 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2050 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2050 | 0.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2020
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2030
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2040
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2020
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2030
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2040
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2025
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2040
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2020 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2025 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2025 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2025 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2030 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2040 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2050 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2050 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2050 | 2000
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 12.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 12.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 20.6
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 4.57
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 12.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 12.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 12.2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 20.6
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 4.57
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2020 | 5.3944
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2025 | 5.3194
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2025 | 9.0055
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2025 | 1.9978
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2030 | 5.2466
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2040 | 5.1757
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2050 | 5.1067
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2050 | 8.6452
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2050 | 1.9179
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2020 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2025 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | lower | 2025 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | upper | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2030 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2040 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2050 | 4
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | lower | 2050 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | upper | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2025 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2025 | 1
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2050 | 3
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2050 | 1
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2020 | 1.71
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2025 | 1.72
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2025 | 1.72
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2025 | 1.72
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2030 | 1.73
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2040 | 1.74
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2050 | 1.75
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2050 | 1.75
45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2050 | 1.75
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2020 | 0.043039
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2025 | 0.043177
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2025 | 0.017214
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2025 | 0.077488
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2030 | 0.04331
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2040 | 0.04356
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2050 | 0.043679
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2050 | 0.017214
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2050 | 0.077488
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2020 | 4.5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2025 | 4.5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2025 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2025 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2030 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2040 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2050 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2050 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2050 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2020 | 0.02
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2025 | 0.02
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2025 | 0.01
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2025 | 0.03
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2030 | 0.02
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2040 | 0.02
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2050 | 0.02
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2050 | 0.01
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2050 | 0.03
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 10.9321
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 10.8971
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 18.45
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 4.1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 10.8636
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 10.8011
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 10.7718
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 18.45
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 4.1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2020 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2025 | 1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2025 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2030 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2040 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2050 | 1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2050 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2025 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2025 | 7
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2050 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2050 | 7
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2020 | 25
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2025 | 25
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2025 | 25
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2025 | 30
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2030 | 30
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2040 | 30
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2050 | 30
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2050 | 25
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2050 | 35
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2020 | 5.4809
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2025 | 5.561
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2025 | 6.5168
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2025 | 4.678
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2030 | 5.6401
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2040 | 5.7959
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2050 | 5.8725
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2050 | 7.0429
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2050 | 4.9432
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 1.6042
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 1.557
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 0.89168
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 2.4146
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 1.5098
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 1.4626
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 1.4155
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 0.81062
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 2.1951
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2020 | 0.55985
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2025 | 0.55951
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2025 | 0.39844
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2025 | 0.79713
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2030 | 0.4793
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2040 | 0.47877
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2050 | 0.47852
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2050 | 0.39299
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2050 | 0.78623
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 0.53473
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 0.519
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 0.30623
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 0.82927
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 0.50327
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 0.48754
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 0.47182
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 0.27839
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 0.75388
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2025 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2025 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2025 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2040 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2050 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2050 | 0
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2020 | 5.4607
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2025 | 5.4529
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2025 | 4.933
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2025 | 5.7724
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2030 | 5.7799
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2040 | 5.8613
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2050 | 5.5142
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2050 | 5.4336
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2050 | 6.1791
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2020 | 23200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2025 | 22500
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2025 | 22500
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2025 | 22500
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2030 | 21800
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2040 | 21100
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2050 | 20500
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2050 | 20500
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2050 | 20500
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.6988
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2025 | 2.6355
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2025 | 1.5964
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2025 | 4.041
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2030 | 2.4924
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2040 | 2.4289
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2050 | 2.3658
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2050 | 1.482
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2050 | 3.7352
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2020 | 5.4607
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2025 | 5.4529
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2025 | 4.933
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2025 | 5.7724
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2030 | 5.7799
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2040 | 5.8613
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2050 | 5.5142
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2050 | 5.4336
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2050 | 6.1791
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2020 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2030 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2040 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2020 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2025 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2025 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2025 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2030 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2040 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2050 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2050 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2050 | 0.2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2020
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2030
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2040
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2020
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2030
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2040
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2025
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2040
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2020 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2025 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2025 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2025 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2030 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2040 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2050 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2050 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2050 | 1200
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 9.41
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 9.41
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 15.88
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 3.53
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 9.41
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 9.41
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 9.41
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 15.88
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 3.53
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2020 | 1.5241
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2025 | 1.4891
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2025 | 2.5135
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2025 | 0.55874
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2030 | 1.4556
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2040 | 1.3931
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2050 | 1.3638
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2050 | 2.3021
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2050 | 0.51173
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2020 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2025 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | lower | 2025 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | upper | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2030 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2040 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2050 | 4
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | lower | 2050 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | upper | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2025 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2025 | 1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2050 | 3
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2050 | 1
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2020 | 6.03
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2025 | 6.1482
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2025 | 6.1482
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2025 | 6.1482
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2030 | 6.2665
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2040 | 6.5029
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2050 | 6.6212
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2050 | 6.6212
45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2050 | 6.6212
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2020 | 0.067497
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2025 | 0.067554
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2025 | 0.038557
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2025 | 0.096617
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2030 | 0.067609
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2040 | 0.067711
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2050 | 0.067759
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2050 | 0.038557
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2050 | 0.096617
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2020 | 4.5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2025 | 4.5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2025 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2025 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2030 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2040 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2050 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2050 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2050 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2020 | 0.02
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2025 | 0.02
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2025 | 0.01
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2025 | 0.03
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2030 | 0.02
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2040 | 0.02
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2050 | 0.02
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2050 | 0.01
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2050 | 0.03
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 12.6523
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 12.6417
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 21.35
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 4.73
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 12.6315
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 12.6124
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 12.6035
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 21.35
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 4.73
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2020 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2025 | 1
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2025 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2030 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2040 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2050 | 1
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2050 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2025 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2025 | 7
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2050 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2050 | 7
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2020 | 25
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2025 | 25
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2025 | 25
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2025 | 30
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2030 | 30
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2040 | 30
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2050 | 30
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2050 | 25
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2050 | 35
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2020 | 11.8542
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2025 | 11.9638
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2025 | 18.297
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2025 | 8.1691
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2030 | 12.0706
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2040 | 12.2757
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2050 | 12.3744
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2050 | 19.3674
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2050 | 8.3762
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 2.0562
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 1.9957
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 1.1438
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 2.948
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 1.9352
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 1.8747
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 1.8143
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 1.0398
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 2.68
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2020 | 0.13408
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2025 | 0.13363
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2025 | 0.095568
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2025 | 0.19158
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2030 | 0.11417
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2040 | 0.11348
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2050 | 0.11316
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2050 | 0.094131
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2050 | 0.1887
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 0.68539
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 0.66523
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 0.39283
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 1.0125
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 0.64507
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 0.62491
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 0.60475
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 0.35711
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 0.92041
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2025 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2025 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2025 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2040 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2050 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2050 | 0
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2020 | 4.3402
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2025 | 4.2484
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2025 | 4.124
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2025 | 4.335
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2030 | 4.2362
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2040 | 4.164
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2050 | 3.9913
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2050 | 3.976
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2050 | 4.1637
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2020 | 24500
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2025 | 23800
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2025 | 23800
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2025 | 23800
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2030 | 23100
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2040 | 22300
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2050 | 21600
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2050 | 21600
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2050 | 21600
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.8756
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2025 | 2.7945
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2025 | 1.6322
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2025 | 4.152
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2030 | 2.6945
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2040 | 2.6131
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2050 | 2.5322
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2050 | 1.4911
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2050 | 3.7891
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2020 | 4.3402
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2025 | 4.2484
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2025 | 4.124
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2025 | 4.335
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2030 | 4.2362
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2040 | 4.164
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2050 | 3.9913
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2050 | 3.976
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2050 | 4.1637
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2020 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2030 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2040 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2020 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2025 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2025 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2025 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2030 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2040 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2050 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2050 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2050 | 0.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2020
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2030
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2040
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2020
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2030
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2040
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2025
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2040
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2020 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2025 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2025 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2025 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2030 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2040 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2050 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2050 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2050 | 2000
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 12.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 12.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 20.58
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 4.57
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 12.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 12.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 12.2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 20.58
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 4.57
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2020 | 0.45733
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2025 | 0.44666
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2025 | 0.75526
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2025 | 0.16771
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2030 | 0.43647
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2040 | 0.41743
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2050 | 0.40852
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2050 | 0.69077
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2050 | 0.15339
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2020 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2025 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | lower | 2025 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | upper | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2030 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2040 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | ctrl | 2050 | 4
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | lower | 2050 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | [L, N] | 1 | upper | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2025 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2025 | 1
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2050 | 3
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2050 | 1
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2020 | 5.57
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2025 | 5.6792
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2025 | 5.6792
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2025 | 5.6792
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2030 | 5.7884
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2040 | 6.0069
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2050 | 6.1161
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2050 | 6.1161
45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2050 | 6.1161
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2015 | 0.003
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2020 | 0.003
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | lower | 2020 | 0.002
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | upper | 2020 | 0.004
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2030 | 0.003
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2050 | 0.003
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | lower | 2050 | 0.002
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | upper | 2050 | 0.004
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050 | 0.25
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | K |  | ctrl | 2015 | 0.005
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | K |  | ctrl | 2020 | 0.005
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | K |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | K |  | upper | 2020 | 0.01
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | K |  | ctrl | 2030 | 0.005
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | K |  | ctrl | 2050 | 0.005
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | K |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | K |  | upper | 2050 | 0.01
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | Space requirement |  | 1000 m2/MWh_h/y |  | J |  | ctrl | 2015 | 6.7
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | Space requirement |  | 1000 m2/MWh_h/y |  | J |  | ctrl | 2020 | 6.3
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | Space requirement |  | 1000 m2/MWh_h/y |  | J |  | lower | 2020 | 6
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | Space requirement |  | 1000 m2/MWh_h/y |  | J |  | upper | 2020 | 6.7
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | Space requirement |  | 1000 m2/MWh_h/y |  | J |  | ctrl | 2030 | 6
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | Space requirement |  | 1000 m2/MWh_h/y |  | J |  | ctrl | 2050 | 5.7
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | Space requirement |  | 1000 m2/MWh_h/y |  | J |  | lower | 2050 | 5.5
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Space requirement [1000 m2/MWh_h/y] | Space requirement |  | 1000 m2/MWh_h/y |  | J |  | upper | 2050 | 6
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | I | 17 | ctrl | 2015 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | I | 17 | ctrl | 2020 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | I | 17 | lower | 2020 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | I | 17 | upper | 2020 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | I | 17 | ctrl | 2030 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | I | 17 | ctrl | 2050 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | I | 17 | lower | 2050 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | I | 17 | upper | 2050 | 30
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | P |  | ctrl | 2015 | 0.43
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | P |  | ctrl | 2020 | 0.45
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | P |  | lower | 2020 | 0.42
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | P |  | upper | 2020 | 0.49
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | P |  | ctrl | 2030 | 0.48
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | P |  | ctrl | 2050 | 0.49946
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | P |  | lower | 2050 | 0.46
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | P |  | upper | 2050 | 0.54
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Typical plant size (collector area) [m2] | Typical plant size | collector area | m2 |  | L |  | ctrl | 2015 | 10000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Typical plant size (collector area) [m2] | Typical plant size | collector area | m2 |  | L |  | ctrl | 2020 | 13000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Typical plant size (collector area) [m2] | Typical plant size | collector area | m2 |  | L |  | lower | 2020 | 10000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Typical plant size (collector area) [m2] | Typical plant size | collector area | m2 |  | L |  | upper | 2020 | 20000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Typical plant size (collector area) [m2] | Typical plant size | collector area | m2 |  | L |  | ctrl | 2030 | 21000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Typical plant size (collector area) [m2] | Typical plant size | collector area | m2 |  | L |  | ctrl | 2050 | 55000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Typical plant size (collector area) [m2] | Typical plant size | collector area | m2 |  | L |  | lower | 2050 | 10000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Typical plant size (collector area) [m2] | Typical plant size | collector area | m2 |  | L |  | upper | 2050 | 100000
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | upper | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | upper | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | O |  | ctrl | 2015 | 0.23464
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | O |  | ctrl | 2020 | 0.22702
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | O |  | lower | 2020 | 0.22316
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | O |  | upper | 2020 | 0.23079
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | O |  | ctrl | 2030 | 0.21872
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | O |  | ctrl | 2050 | 0.20674
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | O |  | lower | 2050 | 0.19407
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | O |  | upper | 2050 | 0.21872
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | O |  | ctrl | 2015 | 0.041143
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | O |  | ctrl | 2020 | 0.039863
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | O |  | lower | 2020 | 0.039673
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | O |  | upper | 2020 | 0.0405
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | O |  | ctrl | 2030 | 0.038346
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | O |  | ctrl | 2050 | 0.036571
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | O |  | lower | 2050 | 0.034433
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | O |  | upper | 2050 | 0.038346
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | R |  | ctrl | 2015 | 0.19
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | R |  | ctrl | 2020 | 0.21
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | R |  | lower | 2020 | 0.14
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | R |  | upper | 2020 | 0.28
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | R |  | ctrl | 2030 | 0.3
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | R |  | ctrl | 2050 | 0.35
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | R |  | lower | 2050 | 0.23
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | R |  | upper | 2050 | 0.47
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2015 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | lower | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | upper | 2020 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2030 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | lower | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | upper | 2050 | 0
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | B |  | ctrl | 2015 | 57.8571
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | B |  | ctrl | 2020 | 60.8085
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | B |  | lower | 2020 | 56.6754
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | B |  | upper | 2020 | 64.2857
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | B |  | ctrl | 2030 | 56.8091
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | B |  | ctrl | 2050 | 59.707
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | B |  | lower | 2050 | 54.7792
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | B |  | upper | 2050 | 56.8091
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, E, H, N, S] | [16, 18] | ctrl | 2015 | 0.31429
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, E, H, N, S] | [16, 18] | ctrl | 2020 | 0.30565
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, E, H, N, S] | [16, 18] | lower | 2020 | 0.2919
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, E, H, N, S] | [16, 18] | upper | 2020 | 0.31964
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, E, H, N, S] | [16, 18] | ctrl | 2030 | 0.29549
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, E, H, N, S] | [16, 18] | ctrl | 2050 | 0.28167
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, E, H, N, S] | [16, 18] | lower | 2050 | 0.25753
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, E, H, N, S] | [16, 18] | upper | 2050 | 0.30543
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (diurnal heat storage) [2015-MEUR/MW_h] | Nominal investment | diurnal heat storage | MEUR/MW_h | 2015 | [D, M] |  | ctrl | 2015 | 0.038571
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (diurnal heat storage) [2015-MEUR/MW_h] | Nominal investment | diurnal heat storage | MEUR/MW_h | 2015 | [D, M] |  | ctrl | 2020 | 0.038512
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (diurnal heat storage) [2015-MEUR/MW_h] | Nominal investment | diurnal heat storage | MEUR/MW_h | 2015 | [D, M] |  | lower | 2020 | 0.029046
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (diurnal heat storage) [2015-MEUR/MW_h] | Nominal investment | diurnal heat storage | MEUR/MW_h | 2015 | [D, M] |  | upper | 2020 | 0.048214
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (diurnal heat storage) [2015-MEUR/MW_h] | Nominal investment | diurnal heat storage | MEUR/MW_h | 2015 | [D, M] |  | ctrl | 2030 | 0.038346
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (diurnal heat storage) [2015-MEUR/MW_h] | Nominal investment | diurnal heat storage | MEUR/MW_h | 2015 | [D, M] |  | ctrl | 2050 | 0.03881
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (diurnal heat storage) [2015-MEUR/MW_h] | Nominal investment | diurnal heat storage | MEUR/MW_h | 2015 | [D, M] |  | lower | 2050 | 0.028955
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (diurnal heat storage) [2015-MEUR/MW_h] | Nominal investment | diurnal heat storage | MEUR/MW_h | 2015 | [D, M] |  | upper | 2050 | 0.048288
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2015 | 0.19
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2020 | 0.21
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2020 | 0.14
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2020 | 0.28
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2030 | 0.3
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2050 | 0.35
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2050 | 0.23
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2050 | 0.47
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2015
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2030
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | F |  | ctrl | 2015
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | F |  | ctrl | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | F |  | lower | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | F |  | upper | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | F |  | ctrl | 2030
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | F |  | ctrl | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | F |  | lower | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | F |  | upper | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2015
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2015
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2020
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector input [MWh_i/m2/y] | Collector input |  | MWh_i/m2/y |  | Q |  | ctrl | 2015 | 1.046
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector input [MWh_i/m2/y] | Collector input |  | MWh_i/m2/y |  | Q |  | ctrl | 2020 | 1.046
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector input [MWh_i/m2/y] | Collector input |  | MWh_i/m2/y |  | Q |  | lower | 2020 | 1.013
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector input [MWh_i/m2/y] | Collector input |  | MWh_i/m2/y |  | Q |  | upper | 2020 | 1.079
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector input [MWh_i/m2/y] | Collector input |  | MWh_i/m2/y |  | Q |  | ctrl | 2030 | 1.046
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector input [MWh_i/m2/y] | Collector input |  | MWh_i/m2/y |  | Q |  | ctrl | 2050 | 1.046
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector input [MWh_i/m2/y] | Collector input |  | MWh_i/m2/y |  | Q |  | lower | 2050 | 1.013
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector input [MWh_i/m2/y] | Collector input |  | MWh_i/m2/y |  | Q |  | upper | 2050 | 1.079
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector output [MWh_h/m2/y] | Collector output |  | MWh_h/m2/y |  | A | 4 | ctrl | 2015 | 0.45
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector output [MWh_h/m2/y] | Collector output |  | MWh_h/m2/y |  | A | 4 | ctrl | 2020 | 0.47296
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector output [MWh_h/m2/y] | Collector output |  | MWh_h/m2/y |  | A | 4 | lower | 2020 | 0.45
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector output [MWh_h/m2/y] | Collector output |  | MWh_h/m2/y |  | A | 4 | upper | 2020 | 0.49591
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector output [MWh_h/m2/y] | Collector output |  | MWh_h/m2/y |  | A | 4 | ctrl | 2030 | 0.49708
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector output [MWh_h/m2/y] | Collector output |  | MWh_h/m2/y |  | A | 4 | ctrl | 2050 | 0.52244
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector output [MWh_h/m2/y] | Collector output |  | MWh_h/m2/y |  | A | 4 | lower | 2050 | 0.49708
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Collector output [MWh_h/m2/y] | Collector output |  | MWh_h/m2/y |  | A | 4 | upper | 2050 | 0.54779
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per annual output) [2015-EUR/MWh_h/y] | Fixed O&M | *total, per annual output | EUR/MWh_h/y | 2015 | B |  | ctrl | 2015 | 0.09
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per annual output) [2015-EUR/MWh_h/y] | Fixed O&M | *total, per annual output | EUR/MWh_h/y | 2015 | B |  | ctrl | 2020 | 0.09
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per annual output) [2015-EUR/MWh_h/y] | Fixed O&M | *total, per annual output | EUR/MWh_h/y | 2015 | B |  | lower | 2020 | 0.08
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per annual output) [2015-EUR/MWh_h/y] | Fixed O&M | *total, per annual output | EUR/MWh_h/y | 2015 | B |  | upper | 2020 | 0.1
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per annual output) [2015-EUR/MWh_h/y] | Fixed O&M | *total, per annual output | EUR/MWh_h/y | 2015 | B |  | ctrl | 2030 | 0.08
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per annual output) [2015-EUR/MWh_h/y] | Fixed O&M | *total, per annual output | EUR/MWh_h/y | 2015 | B |  | ctrl | 2050 | 0.08
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per annual output) [2015-EUR/MWh_h/y] | Fixed O&M | *total, per annual output | EUR/MWh_h/y | 2015 | B |  | lower | 2050 | 0.07
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per annual output) [2015-EUR/MWh_h/y] | Fixed O&M | *total, per annual output | EUR/MWh_h/y | 2015 | B |  | upper | 2050 | 0.08
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per collector area) [2015-EUR/m2/y] | Fixed O&M | *total, per collector area | EUR/m2/y | 2015 | B |  | ctrl | 2015 | 0.0405
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per collector area) [2015-EUR/m2/y] | Fixed O&M | *total, per collector area | EUR/m2/y | 2015 | B |  | ctrl | 2020 | 0.042566
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per collector area) [2015-EUR/m2/y] | Fixed O&M | *total, per collector area | EUR/m2/y | 2015 | B |  | lower | 2020 | 0.039673
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per collector area) [2015-EUR/m2/y] | Fixed O&M | *total, per collector area | EUR/m2/y | 2015 | B |  | upper | 2020 | 0.045
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per collector area) [2015-EUR/m2/y] | Fixed O&M | *total, per collector area | EUR/m2/y | 2015 | B |  | ctrl | 2030 | 0.039766
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per collector area) [2015-EUR/m2/y] | Fixed O&M | *total, per collector area | EUR/m2/y | 2015 | B |  | ctrl | 2050 | 0.041795
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per collector area) [2015-EUR/m2/y] | Fixed O&M | *total, per collector area | EUR/m2/y | 2015 | B |  | lower | 2050 | 0.038345
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Fixed O&M (*total, per collector area) [2015-EUR/m2/y] | Fixed O&M | *total, per collector area | EUR/m2/y | 2015 | B |  | upper | 2050 | 0.039766
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | diurnal heat storage | EUR/MWh_h/y | 2015 | [D, M] |  | ctrl | 2015 | 60
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | diurnal heat storage | EUR/MWh_h/y | 2015 | [D, M] |  | ctrl | 2020 | 57
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | diurnal heat storage | EUR/MWh_h/y | 2015 | [D, M] |  | lower | 2020 | 41
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | diurnal heat storage | EUR/MWh_h/y | 2015 | [D, M] |  | upper | 2020 | 75
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | diurnal heat storage | EUR/MWh_h/y | 2015 | [D, M] |  | ctrl | 2030 | 54
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | diurnal heat storage | EUR/MWh_h/y | 2015 | [D, M] |  | ctrl | 2050 | 52
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | diurnal heat storage | EUR/MWh_h/y | 2015 | [D, M] |  | lower | 2050 | 37
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | diurnal heat storage | EUR/MWh_h/y | 2015 | [D, M] |  | upper | 2050 | 68
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | total solar system excl diurnal heat storage | EUR/MWh_h/y | 2015 | [C, H, N] |  | ctrl | 2015 | 428.8889
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | total solar system excl diurnal heat storage | EUR/MWh_h/y | 2015 | [C, H, N] |  | ctrl | 2020 | 395.3865
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | total solar system excl diurnal heat storage | EUR/MWh_h/y | 2015 | [C, H, N] |  | lower | 2020 | 371.0351
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | total solar system excl diurnal heat storage | EUR/MWh_h/y | 2015 | [C, H, N] |  | upper | 2020 | 422.2222
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | total solar system excl diurnal heat storage | EUR/MWh_h/y | 2015 | [C, H, N] |  | ctrl | 2030 | 362.1148
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | total solar system excl diurnal heat storage | EUR/MWh_h/y | 2015 | [C, H, N] |  | ctrl | 2050 | 325.3987
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | total solar system excl diurnal heat storage | EUR/MWh_h/y | 2015 | [C, H, N] |  | lower | 2050 | 292.0817
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage) [2015-EUR/MWh_h/y] | Nominal investment | total solar system excl diurnal heat storage | EUR/MWh_h/y | 2015 | [C, H, N] |  | upper | 2050 | 362.1148
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [2015-EUR/m2] | Nominal investment | total solar system excl diurnal heat storage, per collector area | EUR/m2 | 2015 | [G, H, N] | 16 | ctrl | 2015 | 193
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [2015-EUR/m2] | Nominal investment | total solar system excl diurnal heat storage, per collector area | EUR/m2 | 2015 | [G, H, N] | 16 | ctrl | 2020 | 187
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [2015-EUR/m2] | Nominal investment | total solar system excl diurnal heat storage, per collector area | EUR/m2 | 2015 | [G, H, N] | 16 | lower | 2020 | 184
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [2015-EUR/m2] | Nominal investment | total solar system excl diurnal heat storage, per collector area | EUR/m2 | 2015 | [G, H, N] | 16 | upper | 2020 | 190
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [2015-EUR/m2] | Nominal investment | total solar system excl diurnal heat storage, per collector area | EUR/m2 | 2015 | [G, H, N] | 16 | ctrl | 2030 | 180
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [2015-EUR/m2] | Nominal investment | total solar system excl diurnal heat storage, per collector area | EUR/m2 | 2015 | [G, H, N] | 16 | ctrl | 2050 | 170
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [2015-EUR/m2] | Nominal investment | total solar system excl diurnal heat storage, per collector area | EUR/m2 | 2015 | [G, H, N] | 16 | lower | 2050 | 160
46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Technology-specific data | Nominal investment (total solar system excl diurnal heat storage, per collector area) [2015-EUR/m2] | Nominal investment | total solar system excl diurnal heat storage, per collector area | EUR/m2 | 2015 | [G, H, N] | 16 | upper | 2050 | 180
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2015 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2020 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2030 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2050 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C |  | ctrl | 2015 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C |  | ctrl | 2020 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C |  | lower | 2020 | 0.33
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C |  | upper | 2020 | 0.37
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C |  | ctrl | 2030 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C |  | ctrl | 2050 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C |  | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C |  | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [1, 2, 3] | ctrl | 2015 | 0.37
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [1, 2, 3] | ctrl | 2020 | 0.37
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [1, 2, 3] | lower | 2020 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [1, 2, 3] | upper | 2020 | 0.39
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [1, 2, 3] | ctrl | 2030 | 0.37
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [1, 2, 3] | ctrl | 2050 | 0.37
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [1, 2, 3] | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [1, 2, 3] | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | ctrl | 2015 | 0.009
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | ctrl | 2020 | 0.009
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | ctrl | 2030 | 0.009
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | ctrl | 2050 | 0.009
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2015 | 18
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2030
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | [D, E] | 5 | ctrl | 2015 | 0.17143
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | [D, E] | 5 | ctrl | 2020 | 0.17143
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | [D, E] | 5 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | [D, E] | 5 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | [D, E] | 5 | ctrl | 2030 | 0.17143
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | [D, E] | 5 | ctrl | 2050 | 0.17143
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | [D, E] | 5 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | [D, E] | 5 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2015 | 25
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2020 | 25
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2030 | 25
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2050 | 25
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 8 | ctrl | 2015 | 24
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 8 | ctrl | 2020 | 24
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 8 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 8 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 8 | ctrl | 2030 | 24
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 8 | ctrl | 2050 | 24
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 8 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 8 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 8 | ctrl | 2015 | 2.1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 8 | ctrl | 2020 | 2.1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 8 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 8 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 8 | ctrl | 2030 | 2.1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 8 | ctrl | 2050 | 2.1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 8 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 8 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 8 | ctrl | 2015 | 942
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 8 | ctrl | 2020 | 942
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 8 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 8 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 8 | ctrl | 2030 | 942
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 8 | ctrl | 2050 | 942
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 8 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 8 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | ctrl | 2015 | 5
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | ctrl | 2020 | 5
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | ctrl | 2030 | 5
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | ctrl | 2050 | 5
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | I | 8 | ctrl | 2015 | 23
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | I | 8 | ctrl | 2020 | 23
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | I | 8 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | I | 8 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | I | 8 | ctrl | 2030 | 23
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | I | 8 | ctrl | 2050 | 23
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | I | 8 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | I | 8 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | L |  | ctrl | 2015 | 0.2275
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | L |  | ctrl | 2020 | 0.22295
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | L |  | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | L |  | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | L |  | ctrl | 2030 | 0.22295
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | L |  | ctrl | 2050 | 0.2184
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | L |  | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | L |  | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | L |  | ctrl | 2015 | 0.1225
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | L |  | ctrl | 2020 | 0.12005
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | L |  | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | L |  | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | L |  | ctrl | 2030 | 0.12005
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | L |  | ctrl | 2050 | 0.1176
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | L |  | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | L |  | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, P, Q] | 6 | ctrl | 2015 | 8800
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, P, Q] | 6 | ctrl | 2020 | 8800
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, P, Q] | 6 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, P, Q] | 6 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, P, Q] | 6 | ctrl | 2030 | 8448
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, P, Q] | 6 | ctrl | 2050 | 8096
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, P, Q] | 6 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, P, Q] | 6 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [1, 6, 9, 10] | ctrl | 2015 | 0.35
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [1, 6, 9, 10] | ctrl | 2020 | 0.343
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [1, 6, 9, 10] | lower | 2020 | 0.2744
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [1, 6, 9, 10] | upper | 2020 | 0.4116
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [1, 6, 9, 10] | ctrl | 2030 | 0.343
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [1, 6, 9, 10] | ctrl | 2050 | 0.336
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [1, 6, 9, 10] | lower | 2050 | 0.2352
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [1, 6, 9, 10] | upper | 2050 | 0.4368
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | R | [6, 11] | ctrl | 2015
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | R | [6, 11] | ctrl | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | R | [6, 11] | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | R | [6, 11] | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | R | [6, 11] | ctrl | 2030
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | R | [6, 11] | ctrl | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | R | [6, 11] | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | R | [6, 11] | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [11, 12, 13] | ctrl | 2015 | 6
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [11, 12, 13] | ctrl | 2020 | 6
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [11, 12, 13] | lower | 2020 | 2.6
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [11, 12, 13] | upper | 2020 | 8.5
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [11, 12, 13] | ctrl | 2030 | 6
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [11, 12, 13] | ctrl | 2050 | 6
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [11, 12, 13] | lower | 2050 | 2.6
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [11, 12, 13] | upper | 2050 | 8.5
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | H | 6 | ctrl | 2015 | 0.085
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | H | 6 | ctrl | 2020 | 0.085
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | H | 6 | lower | 2020 | 0.051
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | H | 6 | upper | 2020 | 0.17
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | H | 6 | ctrl | 2030 | 0.085
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | H | 6 | ctrl | 2050 | 0.085
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | H | 6 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | H | 6 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | ctrl | 2015 | 0.01
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | ctrl | 2020 | 0.01
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | ctrl | 2030 | 0.01
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | ctrl | 2050 | 0.01
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F | 6 | ctrl | 2015 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F | 6 | ctrl | 2020 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F | 6 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F | 6 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F | 6 | ctrl | 2030 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F | 6 | ctrl | 2050 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F | 6 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F | 6 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | F | 6 | ctrl | 2015 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | F | 6 | ctrl | 2020 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | F | 6 | lower | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | F | 6 | upper | 2020
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | F | 6 | ctrl | 2030 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | F | 6 | ctrl | 2050 | 1
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | F | 6 | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | F | 6 | upper | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [6, 7] | ctrl | 2015 | 0.016667
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [6, 7] | ctrl | 2020 | 0.016667
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [6, 7] | lower | 2020 | 0.0083333
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [6, 7] | upper | 2020 | 0.033333
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [6, 7] | ctrl | 2030 | 0.016667
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [6, 7] | ctrl | 2050 | 0.016667
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [6, 7] | lower | 2050
50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [6, 7] | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [4, 5] | ctrl | 2015 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [4, 5] | ctrl | 2020 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [4, 5] | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [4, 5] | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [4, 5] | ctrl | 2030 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [4, 5] | ctrl | 2050 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [4, 5] | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [4, 5] | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | D | 2 | ctrl | 2015 | 0.46
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | D | 2 | ctrl | 2020 | 0.46
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | D | 2 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | D | 2 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | D | 2 | ctrl | 2030 | 0.48
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | D | 2 | ctrl | 2050 | 0.48
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | D | 2 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | D | 2 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | 1 | ctrl | 2015 | 0.48
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | 1 | ctrl | 2020 | 0.48
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | 1 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | 1 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | 1 | ctrl | 2030 | 0.5
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | 1 | ctrl | 2050 | 0.5
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | 1 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | 1 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | ctrl | 2015 | 0.009
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | ctrl | 2020 | 0.009
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | ctrl | 2030 | 0.009
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | ctrl | 2050 | 0.009
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2015 | 200
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2020 | 200
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2030 | 200
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2050 | 200
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E |  | ctrl | 2015 | 0.028571
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E |  | ctrl | 2020 | 0.028571
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E |  | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E |  | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E |  | ctrl | 2030 | 0.028571
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E |  | ctrl | 2050 | 0.028571
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E |  | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E |  | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | F |  | ctrl | 2015 | 25
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | F |  | ctrl | 2020 | 25
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | F |  | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | F |  | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | F |  | ctrl | 2030 | 25
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | F |  | ctrl | 2050 | 25
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | F |  | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | F |  | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 2 | ctrl | 2015 | 315
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 2 | ctrl | 2020 | 315
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 2 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 2 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 2 | ctrl | 2030 | 315
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 2 | ctrl | 2050 | 315
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 2 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 2 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 2 | ctrl | 2015 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 2 | ctrl | 2020 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 2 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 2 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 2 | ctrl | 2030 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 2 | ctrl | 2050 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 2 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 2 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 2 | ctrl | 2015 | 75
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 2 | ctrl | 2020 | 75
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 2 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 2 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 2 | ctrl | 2030 | 75
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 2 | ctrl | 2050 | 75
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 2 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 2 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | ctrl | 2015 | 0.76
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | ctrl | 2020 | 0.76
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | ctrl | 2030 | 0.76
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | ctrl | 2050 | 0.76
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 8 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | F | 2 | ctrl | 2015 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | F | 2 | ctrl | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | F | 2 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | F | 2 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | F | 2 | ctrl | 2030 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | F | 2 | ctrl | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | F | 2 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | F | 2 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | F | 2 | ctrl | 2015 | 0.3315
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | F | 2 | ctrl | 2020 | 0.32155
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | F | 2 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | F | 2 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | F | 2 | ctrl | 2030 | 0.30829
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | F | 2 | ctrl | 2050 | 0.29172
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | F | 2 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | F | 2 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | F | 2 | ctrl | 2015 | 0.1785
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | F | 2 | ctrl | 2020 | 0.17314
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | F | 2 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | F | 2 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | F | 2 | ctrl | 2030 | 0.16601
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | F | 2 | ctrl | 2050 | 0.15708
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | F | 2 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | F | 2 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [O, P] | 7 | ctrl | 2015 | 6500
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [O, P] | 7 | ctrl | 2020 | 6500
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [O, P] | 7 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [O, P] | 7 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [O, P] | 7 | ctrl | 2030 | 6250
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [O, P] | 7 | ctrl | 2050 | 6000
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [O, P] | 7 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [O, P] | 7 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [L, M, N, R] | [7, 5, 9] | ctrl | 2015 | 0.51
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [L, M, N, R] | [7, 5, 9] | ctrl | 2020 | 0.4947
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [L, M, N, R] | [7, 5, 9] | lower | 2020 | 0.39576
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [L, M, N, R] | [7, 5, 9] | upper | 2020 | 0.59364
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [L, M, N, R] | [7, 5, 9] | ctrl | 2030 | 0.4743
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [L, M, N, R] | [7, 5, 9] | ctrl | 2050 | 0.4488
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [L, M, N, R] | [7, 5, 9] | lower | 2050 | 0.31416
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [L, M, N, R] | [7, 5, 9] | upper | 2050 | 0.58344
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | Q | 10 | ctrl | 2015 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | Q | 10 | ctrl | 2020 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | Q | 10 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | Q | 10 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | Q | 10 | ctrl | 2030 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | Q | 10 | ctrl | 2050 | 0
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | Q | 10 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 | Q | 10 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [10, 11, 12] | ctrl | 2015 | 6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [10, 11, 12] | ctrl | 2020 | 6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [10, 11, 12] | lower | 2020 | 2.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [10, 11, 12] | upper | 2020 | 8.5
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [10, 11, 12] | ctrl | 2030 | 6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [10, 11, 12] | ctrl | 2050 | 6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [10, 11, 12] | lower | 2050 | 2.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [10, 11, 12] | upper | 2050 | 8.5
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | I | 7 | ctrl | 2015 | 0.17
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | I | 7 | ctrl | 2020 | 0.17
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | I | 7 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | I | 7 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | I | 7 | ctrl | 2030 | 0.17
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | I | 7 | ctrl | 2050 | 0.17
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | I | 7 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | I | 7 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [6, 7] | ctrl | 2015 | 0.015
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [6, 7] | ctrl | 2020 | 0.015
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [6, 7] | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [6, 7] | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [6, 7] | ctrl | 2030 | 0.015
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [6, 7] | ctrl | 2050 | 0.015
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [6, 7] | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [6, 7] | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 6 | ctrl | 2015 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 6 | ctrl | 2020 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 6 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 6 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 6 | ctrl | 2030 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 6 | ctrl | 2050 | 0.6
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 6 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 6 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | 6 | ctrl | 2015 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | 6 | ctrl | 2020 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | 6 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | 6 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | 6 | ctrl | 2030 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | 6 | ctrl | 2050 | 1
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | 6 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | 6 | upper | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | I | 7 | ctrl | 2015 | 0.033333
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | I | 7 | ctrl | 2020 | 0.033333
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | I | 7 | lower | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | I | 7 | upper | 2020
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | I | 7 | ctrl | 2030 | 0.033333
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | I | 7 | ctrl | 2050 | 0.033333
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | I | 7 | lower | 2050
51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | I | 7 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 5 | ctrl | 2015 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 5 | ctrl | 2020 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 5 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 5 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 5 | ctrl | 2030 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 5 | ctrl | 2050 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 5 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 5 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C | 3 | ctrl | 2015 | 0.39
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C | 3 | ctrl | 2020 | 0.4
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C | 3 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C | 3 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C | 3 | ctrl | 2030 | 0.41
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C | 3 | ctrl | 2050 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C | 3 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | C | 3 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [B, C] | [1, 2] | ctrl | 2015 | 0.41
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [B, C] | [1, 2] | ctrl | 2020 | 0.42
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [B, C] | [1, 2] | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [B, C] | [1, 2] | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [B, C] | [1, 2] | ctrl | 2030 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [B, C] | [1, 2] | ctrl | 2050 | 0.45
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [B, C] | [1, 2] | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [B, C] | [1, 2] | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | ctrl | 2015 | 0.0137
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | ctrl | 2020 | 0.0137
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | ctrl | 2030 | 0.0137
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | ctrl | 2050 | 0.0137
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 4 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 100
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 100
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 100
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 100
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D | 1 | ctrl | 2015 | 0.10714
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D | 1 | ctrl | 2020 | 0.10714
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D | 1 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D | 1 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D | 1 | ctrl | 2030 | 0.10714
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D | 1 | ctrl | 2050 | 0.10714
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D | 1 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D | 1 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | 3 | ctrl | 2015 | 25
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | 3 | ctrl | 2020 | 25
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | 3 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | 3 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | 3 | ctrl | 2030 | 25
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | 3 | ctrl | 2050 | 25
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | 3 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | 3 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 11 | ctrl | 2015 | 1.7
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 11 | ctrl | 2020 | 1.7
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 11 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 11 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 11 | ctrl | 2030 | 1.7
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 11 | ctrl | 2050 | 1.7
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 11 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 11 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 11 | ctrl | 2015 | 1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 11 | ctrl | 2020 | 1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 11 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 11 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 11 | ctrl | 2030 | 1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 11 | ctrl | 2050 | 1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 11 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 11 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 11 | ctrl | 2015 | 48
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 11 | ctrl | 2020 | 48
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 11 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 11 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 11 | ctrl | 2030 | 48
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 11 | ctrl | 2050 | 48
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 11 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 11 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 11 | ctrl | 2015 | 0.1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 11 | ctrl | 2020 | 0.1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 11 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 11 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 11 | ctrl | 2030 | 0.1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 11 | ctrl | 2050 | 0.1
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 11 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 11 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  | 11 | ctrl | 2015 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  | 11 | ctrl | 2020 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  | 11 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  | 11 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  | 11 | ctrl | 2030 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  | 11 | ctrl | 2050 | 0.43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  | 11 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  | 11 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 12 | ctrl | 2015 | 0.36504
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 12 | ctrl | 2020 | 0.35409
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 12 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 12 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 12 | ctrl | 2030 | 0.33949
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 12 | ctrl | 2050 | 0.32124
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 12 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 12 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 12 | ctrl | 2015 | 0.10296
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 12 | ctrl | 2020 | 0.099871
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 12 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 12 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 12 | ctrl | 2030 | 0.095753
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 12 | ctrl | 2050 | 0.090605
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 12 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 12 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | P | 9 | ctrl | 2015 | 8068
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | P | 9 | ctrl | 2020 | 8068
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | P | 9 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | P | 9 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | P | 9 | ctrl | 2030 | 7745.28
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | P | 9 | ctrl | 2050 | 7422.56
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | P | 9 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | P | 9 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [7, 9, 10] | ctrl | 2015 | 0.468
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [7, 9, 10] | ctrl | 2020 | 0.45396
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [7, 9, 10] | lower | 2020 | 0.36317
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [7, 9, 10] | upper | 2020 | 0.54475
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [7, 9, 10] | ctrl | 2030 | 0.43524
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [7, 9, 10] | ctrl | 2050 | 0.41184
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [7, 9, 10] | lower | 2050 | 0.28829
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [7, 9, 10] | upper | 2050 | 0.53539
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  | 9 | ctrl | 2015 | 43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  | 9 | ctrl | 2020 | 43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  | 9 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  | 9 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  | 9 | ctrl | 2030 | 43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  | 9 | ctrl | 2050 | 43
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  | 9 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  | 9 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [5, 9, 10] | ctrl | 2015 | 4.5
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [5, 9, 10] | ctrl | 2020 | 4.5
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [5, 9, 10] | lower | 2020 | 3.5
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [5, 9, 10] | upper | 2020 | 5
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [5, 9, 10] | ctrl | 2030 | 4.5
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [5, 9, 10] | ctrl | 2050 | 4.5
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [5, 9, 10] | lower | 2050 | 3.5
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | [5, 9, 10] | upper | 2050 | 5
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | L | [1, 6, 8] | ctrl | 2015 | 0.17
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | L | [1, 6, 8] | ctrl | 2020 | 0.17
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | L | [1, 6, 8] | lower | 2020 | 0.119
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | L | [1, 6, 8] | upper | 2020 | 0.187
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | L | [1, 6, 8] | ctrl | 2030 | 0.17
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | L | [1, 6, 8] | ctrl | 2050 | 0.17
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | L | [1, 6, 8] | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | L | [1, 6, 8] | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | I | 8 | ctrl | 2015 | 0.25
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | I | 8 | ctrl | 2020 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | I | 8 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | I | 8 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | I | 8 | ctrl | 2030 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | I | 8 | ctrl | 2050 | 0.2
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | I | 8 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | I | 8 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 5 | ctrl | 2015 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 5 | ctrl | 2020 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 5 | lower | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 5 | upper | 2020
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 5 | ctrl | 2030 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 5 | ctrl | 2050 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 5 | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | 5 | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [5, 6, 7] | ctrl | 2015 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [5, 6, 7] | ctrl | 2020 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [5, 6, 7] | lower | 2020 | 0.15
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [5, 6, 7] | upper | 2020 | 0.5
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [5, 6, 7] | ctrl | 2030 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [5, 6, 7] | ctrl | 2050 | 0.3
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [5, 6, 7] | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [5, 6, 7] | upper | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [8, 9, 10] | ctrl | 2015 | 0.083333
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [8, 9, 10] | ctrl | 2020 | 0.083333
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [8, 9, 10] | lower | 2020 | 0.075
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [8, 9, 10] | upper | 2020 | 0.10833
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [8, 9, 10] | ctrl | 2030 | 0.083333
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [8, 9, 10] | ctrl | 2050 | 0.083333
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [8, 9, 10] | lower | 2050
52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [8, 9, 10] | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | 18 | ctrl | 2015 | 0.38
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | 18 | ctrl | 2020 | 0.39
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | 18 | lower | 2020 | 0.385
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | 18 | upper | 2020 | 0.4
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | 18 | ctrl | 2030 | 0.4
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | 18 | ctrl | 2050 | 0.42
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | 18 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | 18 | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 18 | ctrl | 2015 | 0.04
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 18 | ctrl | 2020 | 0.41
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 18 | lower | 2020 | 0.405
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 18 | upper | 2020 | 0.42
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 18 | ctrl | 2030 | 0.42
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 18 | ctrl | 2050 | 0.44
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 18 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 18 | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | B | 11 | ctrl | 2015 | 3
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | B | 11 | ctrl | 2020 | 3
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | B | 11 | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | B | 11 | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | B | 11 | ctrl | 2030 | 3
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | B | 11 | ctrl | 2050 | 3
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | B | 11 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | B | 11 | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | B | 11 | ctrl | 2015 | 0.6
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | B | 11 | ctrl | 2020 | 0.6
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | B | 11 | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | B | 11 | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | B | 11 | ctrl | 2030 | 0.6
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | B | 11 | ctrl | 2050 | 0.6
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | B | 11 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | B | 11 | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | 11 | ctrl | 2015 | 230
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | 11 | ctrl | 2020 | 230
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | 11 | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | 11 | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | 11 | ctrl | 2030 | 230
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | 11 | ctrl | 2050 | 230
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | 11 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | 11 | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | B | 11 | ctrl | 2015 | 5
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | B | 11 | ctrl | 2020 | 5
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | B | 11 | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | B | 11 | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | B | 11 | ctrl | 2030 | 5
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | B | 11 | ctrl | 2050 | 5
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | B | 11 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | B | 11 | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | B | 11 | ctrl | 2015 | 23
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | B | 11 | ctrl | 2020 | 23
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | B | 11 | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | B | 11 | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | B | 11 | ctrl | 2030 | 23
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | B | 11 | ctrl | 2050 | 23
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | B | 11 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | B | 11 | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 20 | ctrl | 2015 | 0.3042
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 20 | ctrl | 2020 | 0.29507
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 20 | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 20 | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 20 | ctrl | 2030 | 0.28291
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 20 | ctrl | 2050 | 0.2677
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 20 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 20 | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 20 | ctrl | 2015 | 0.0858
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 20 | ctrl | 2020 | 0.083226
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 20 | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 20 | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 20 | ctrl | 2030 | 0.079794
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 20 | ctrl | 2050 | 0.075504
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 20 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 20 | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, D] | 19 | ctrl | 2015 | 0.39
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, D] | 19 | ctrl | 2020 | 0.3783
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, D] | 19 | lower | 2020 | 0.30264
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, D] | 19 | upper | 2020 | 0.45396
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, D] | 19 | ctrl | 2030 | 0.3627
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, D] | 19 | ctrl | 2050 | 0.3432
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, D] | 19 | lower | 2050 | 0.24024
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, D] | 19 | upper | 2050 | 0.44616
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | A | 18 | ctrl | 2015 | 0.1785
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | A | 18 | ctrl | 2020 | 0.1785
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | A | 18 | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | A | 18 | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | A | 18 | ctrl | 2030 | 0.1785
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | A | 18 | ctrl | 2050 | 0.1785
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | A | 18 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | A | 18 | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2015
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | A | 18 | ctrl | 2015 | 0.091667
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | A | 18 | ctrl | 2020 | 0.091667
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | A | 18 | lower | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | A | 18 | upper | 2020
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | A | 18 | ctrl | 2030 | 0.091667
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | A | 18 | ctrl | 2050 | 0.091667
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | A | 18 | lower | 2050
52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | A | 18 | upper | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | lower | 2020 | 0.001
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | lower | 2050 | 0.001
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2015 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2020 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | upper | 2020 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2030 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2050 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | upper | 2050 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.005
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.01
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2015 | 0.98
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | lower | 2020 | 0.98
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | ctrl | 2015 | 0.98
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | lower | 2020 | 0.98
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2020 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | upper | 2020 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2030 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | lower | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | upper | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | ctrl | 2020 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | upper | 2020 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | ctrl | 2030 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | ctrl | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | lower | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | upper | 2050 | 0.99
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2015 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2015 | 5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2020 | 5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2020 | 25
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2030 | 5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2050 | 5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2050 | 25
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2015 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2020 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2020 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2020 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2030 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2050 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2050 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2050 | 20
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2015 | 0.008
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020 | 0.008
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2020 | 0.008
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2020 | 0.008
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030 | 0.008
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050 | 0.008
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050 | 0.008
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050 | 0.008
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2015 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2020 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2020 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2020 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2030 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2050 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2050 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2050 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2015
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | lower | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | upper | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | lower | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | upper | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2015
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2015
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2015
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2015
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | ctrl | 2015 | 0.15
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | ctrl | 2020 | 0.15
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | lower | 2020 | 0.1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | upper | 2020 | 0.25
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | ctrl | 2030 | 0.14
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | ctrl | 2050 | 0.13
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | lower | 2050 | 0.1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | upper | 2050 | 0.25
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | ctrl | 2015 | 0.12
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | ctrl | 2020 | 0.11703
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | lower | 2020 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | upper | 2020 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | ctrl | 2030 | 0.11131
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | ctrl | 2050 | 0.10069
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | lower | 2050 | 0.08
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | upper | 2050 | 0.2
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | ctrl | 2015 | 0.03
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | ctrl | 2020 | 0.029257
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | lower | 2020 | 0.02
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | upper | 2020 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | ctrl | 2030 | 0.027827
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | ctrl | 2050 | 0.025173
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | lower | 2050 | 0.02
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | upper | 2050 | 0.05
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2015 | 1100
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2020 | 1070
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2020 | 1000
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2020 | 1100
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2030 | 1020
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2050 | 920
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2050 | 900
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2050 | 1000
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2015 | 0.8
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2020 | 0.9
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2020 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2020 | 0.9
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2030 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2050 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2050 | 1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | ctrl | 2015 | 0.3
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | ctrl | 2020 | 0.3
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | lower | 2020 | 0.1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | upper | 2020 | 0.3
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | ctrl | 2030 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | ctrl | 2050 | 0.6
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | lower | 2050 | 0.1
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | upper | 2050 | 0.6
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2015 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2020 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | lower | 2020 | 0.4
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | upper | 2020 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2030 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2050 | 0.4
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | lower | 2050 | 0.3
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | upper | 2050 | 0.5
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | ctrl | 2015 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | ctrl | 2020 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | lower | 2020 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | upper | 2020 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | ctrl | 2030 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | lower | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | upper | 2030
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | ctrl | 2050 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | lower | 2050 | 0
41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | upper | 2050 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | lower | 2020 | 0.001
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | lower | 2050 | 0.001
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2015 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2020 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | upper | 2020 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2030 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | ctrl | 2050 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | upper | 2050 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.005
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2015 | 0.98
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | lower | 2020 | 0.98
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | ctrl | 2015 | 0.98
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | lower | 2020 | 0.98
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2020 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | upper | 2020 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2030 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | lower | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | upper | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | ctrl | 2020 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | upper | 2020 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | ctrl | 2030 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | ctrl | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | lower | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | upper | 2050 | 0.99
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2015 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2015 | 5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2020 | 5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2020 | 25
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2030 | 5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2050 | 5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2050 | 25
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 0.2
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2015 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2020 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2020 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2020 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2030 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2050 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2050 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2050 | 20
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2015 | 0.008
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020 | 0.008
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2020 | 0.008
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2020 | 0.008
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030 | 0.008
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050 | 0.008
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050 | 0.008
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050 | 0.008
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2015 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2020 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2020 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2020 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2030 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2050 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2050 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2050 | 0.08
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2015
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | lower | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | upper | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | lower | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | upper | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2015
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2015
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2015
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2015
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | ctrl | 2015 | 0.07
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | ctrl | 2020 | 0.07
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | lower | 2020 | 0.02
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | upper | 2020 | 0.17
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | ctrl | 2030 | 0.06
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | ctrl | 2050 | 0.06
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | lower | 2050 | 0.02
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | upper | 2050 | 0.17
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | ctrl | 2015 | 0.06
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | ctrl | 2020 | 0.058515
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | lower | 2020 | 0.02
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | upper | 2020 | 0.14
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | ctrl | 2030 | 0.05
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | ctrl | 2050 | 0.050345
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | lower | 2050 | 0.02
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  |  | upper | 2050 | 0.14
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | ctrl | 2015 | 0.01
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | ctrl | 2020 | 0.0097525
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | upper | 2020 | 0.03
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | ctrl | 2030 | 0.0092757
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | ctrl | 2050 | 0.0083909
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | upper | 2050 | 0.03
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2015 | 1100
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2020 | 1070
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2020 | 1000
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2020 | 1100
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2030 | 1020
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2050 | 920
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2050 | 900
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2050 | 1000
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2015 | 0.8
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2020 | 0.9
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2020 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2020 | 0.9
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2030 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2050 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2050 | 1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | ctrl | 2015 | 0.3
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | ctrl | 2020 | 0.3
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | lower | 2020 | 0.1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | upper | 2020 | 0.3
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | ctrl | 2030 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | ctrl | 2050 | 0.6
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | lower | 2050 | 0.1
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 |  |  | upper | 2050 | 0.6
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2015 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2020 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | lower | 2020 | 0.4
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | upper | 2020 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2030 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | ctrl | 2050 | 0.4
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | lower | 2050 | 0.3
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  |  | upper | 2050 | 0.5
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | ctrl | 2015 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | ctrl | 2020 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | lower | 2020 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | upper | 2020 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | ctrl | 2030 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | lower | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | upper | 2030
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | ctrl | 2050 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | lower | 2050 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Technology-specific data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 |  |  | upper | 2050 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | lower | 2020 | 0
41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  |  | lower | 2050 | 0
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020 | 3
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020 | 4
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020 | 2
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020 | 50
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Length of installation of one power plant [km] | Length of installation of one power plant |  | km |  |  |  | lower | 2020 | 0.2
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Length of installation of one power plant [km] | Length of installation of one power plant |  | km |  |  |  | upper | 2020 | 5
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | lower | 2020 | 3.8
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | upper | 2020 | 9
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050 | 3
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050 | 4
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050 | 50
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050 | 500
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Length of installation of one power plant [km] | Length of installation of one power plant |  | km |  |  |  | lower | 2050 | 5
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Length of installation of one power plant [km] | Length of installation of one power plant |  | km |  |  |  | upper | 2050 | 100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2040 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2040 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B3,C |  | ctrl | 2015 | 0.006
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B3,C |  | ctrl | 2020 | 0.006
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B3,C |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B3,C |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B3,C |  | ctrl | 2030 | 0.006
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B3,C |  | ctrl | 2040 | 0.006
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B3,C |  | ctrl | 2050 | 0.006
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B3,C |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B3,C |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2040 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 0
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | ctrl | 2015 | 6.3636
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | ctrl | 2020 | 5.122
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | ctrl | 2030 | 4.5652
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | ctrl | 2040 | 4.2857
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | ctrl | 2050 | 4.0385
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2015 | 30
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2020 | 35
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2030 | 40
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2040 | 40
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2050 | 40
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | ctrl | 2015 | 16700
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | ctrl | 2020 | 13400
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | lower | 2020 | 12100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | upper | 2020 | 14800
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | ctrl | 2030 | 10700
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | ctrl | 2040 | 9600
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | ctrl | 2050 | 8900
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | lower | 2050 | 8100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | upper | 2050 | 9900
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | ctrl | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | ctrl | 2030
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | ctrl | 2040
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | ctrl | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2015 | 1.6723
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2020 | 1.2419
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | lower | 2020 | 1.1855
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | upper | 2020 | 1.2984
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2030 | 0.84005
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2040 | 0.69912
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2050 | 0.63581
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | lower | 2050 | 0.54163
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | upper | 2050 | 0.84645
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2015 | 1.5927
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2020 | 1.1828
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | lower | 2020 | 1.129
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | upper | 2020 | 1.2366
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2030 | 0.80004
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2040 | 0.66583
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2050 | 0.60554
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | lower | 2050 | 0.51584
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | upper | 2050 | 0.80615
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2040
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2040
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | ctrl | 2015 | 0.005
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | ctrl | 2020 | 0.004
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | ctrl | 2030 | 0.003
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | ctrl | 2040 | 0.003
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | ctrl | 2050 | 0.003
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | ctrl | 2015 | 934.7208
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | ctrl | 2020 | 1010.328
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | ctrl | 2030 | 1116.06
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | ctrl | 2040 | 1127.808
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | ctrl | 2050 | 1139.556
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2015 | 981.4568
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2020 | 1060.8444
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2030 | 1171.863
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2040 | 1184.1984
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2050 | 1196.5338
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | ctrl | 2015 | 15900
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | ctrl | 2020 | 12800
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | lower | 2020 | 11500
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | upper | 2020 | 14100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | ctrl | 2030 | 10200
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | ctrl | 2040 | 9100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | ctrl | 2050 | 8500
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | lower | 2050 | 7700
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | upper | 2050 | 9400
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2030
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2040
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2020 | 12800
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2030 | 10200
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2040 | 9100
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2050 | 8500
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B3,C |  | ctrl | 2015 | 0.0063
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B3,C |  | ctrl | 2020 | 0.0063
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B3,C |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B3,C |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B3,C |  | ctrl | 2030 | 0.0063
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B3,C |  | ctrl | 2040 | 0.0063
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B3,C |  | ctrl | 2050 | 0.0063
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B3,C |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B3,C |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2015 | 1068
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2020 | 1068
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2030 | 1068
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2040 | 1068
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2050 | 1068
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2015 | 10
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2020 | 12.5
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2030 | 15
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2040 | 15
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2050 | 15
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.031299
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.029877
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.032722
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.025216
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.022635
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.021371
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.019012
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.023704
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.22318
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.21303
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.23332
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.14485
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.11672
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.10405
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.086266
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.12244
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | ctrl | 2015 | 0.81387
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | ctrl | 2020 | 0.49112
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | lower | 2020 | 0.4688
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | upper | 2020 | 0.51345
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | ctrl | 2030 | 0.27221
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | ctrl | 2040 | 0.20271
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | ctrl | 2050 | 0.17327
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | lower | 2050 | 0.13645
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | upper | 2050 | 0.32639
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.26915
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.25691
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.28138
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.21683
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.19464
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.18377
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.16349
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.20383
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.21255
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.20289
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.22221
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.13796
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.11116
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.099095
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.082158
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.11661
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.81759
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.20108
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.19194
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.21022
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.16199
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.14541
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.13729
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.12214
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.15228
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.85846
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.21113
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.20153
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.22073
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.17009
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.15268
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.14416
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.12824
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.1599
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | ctrl | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | ctrl | 2030
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | ctrl | 2040
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | ctrl | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | ctrl | 2015 | 0.77511
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | ctrl | 2020 | 0.46774
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | lower | 2020 | 0.44647
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | upper | 2020 | 0.489
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | ctrl | 2030 | 0.25925
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | ctrl | 2040 | 0.19306
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | ctrl | 2050 | 0.16502
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | lower | 2050 | 0.12995
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | upper | 2050 | 0.31085
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.029809
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.028454
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.031164
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.024015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.021557
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.020353
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.018107
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.022575
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2015 | 0.165
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2020 | 0.205
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2030 | 0.23
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2040 | 0.245
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2050 | 0.26
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | ctrl | 2015
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | ctrl | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | ctrl | 2030
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | ctrl | 2040
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | ctrl | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2015 | 0.79
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2020 | 0.86
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2030 | 0.95
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2040 | 0.96
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2050 | 0.97
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2015 | 1.05
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2020 | 1.05
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2030 | 1.05
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2040 | 1.05
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2050 | 1.05
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  |  | 6 | ctrl | 2015 | 6.0606
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  |  | 6 | ctrl | 2020 | 4.878
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  |  | 6 | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  |  | 6 | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  |  | 6 | ctrl | 2030 | 4.3478
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  |  | 6 | ctrl | 2040 | 4.0816
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  |  | 6 | ctrl | 2050 | 3.8462
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  |  | 6 | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  |  | 6 | upper | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2015 | 1.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2020 | 1.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | lower | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | upper | 2020
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2030 | 1.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2040 | 1.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2050 | 1.1
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | lower | 2050
22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2040 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2040 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B2,C |  | ctrl | 2015 | 0.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B2,C |  | ctrl | 2020 | 0.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B2,C |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B2,C |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B2,C |  | ctrl | 2030 | 0.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B2,C |  | ctrl | 2040 | 0.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B2,C |  | ctrl | 2050 | 0.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B2,C |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | B2,C |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2040 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | ctrl | 2015 | 6.6667
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | ctrl | 2020 | 5.3659
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | ctrl | 2030 | 4.7826
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | ctrl | 2040 | 4.4898
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | ctrl | 2050 | 4.2308
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 6 | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2015 | 30
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2020 | 35
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2030 | 40
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2040 | 40
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2050 | 40
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | ctrl | 2015 | 14300
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | ctrl | 2020 | 10600
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | lower | 2020 | 9500
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | upper | 2020 | 11700
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | ctrl | 2030 | 8900
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | ctrl | 2040 | 8000
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | ctrl | 2050 | 7500
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | lower | 2050 | 6700
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P |  | upper | 2050 | 8300
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | ctrl | 2015
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | ctrl | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | ctrl | 2030
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | ctrl | 2040
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | ctrl | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2015 | 1.4274
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2020 | 0.87231
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | lower | 2020 | 0.85753
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | upper | 2020 | 0.92406
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2030 | 0.56581
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2040 | 0.46052
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2050 | 0.4139
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | lower | 2050 | 0.35795
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | upper | 2050 | 0.58766
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2015 | 1.2976
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2020 | 0.79301
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | lower | 2020 | 0.77957
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | upper | 2020 | 0.84005
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2030 | 0.51437
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2040 | 0.41865
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | ctrl | 2050 | 0.37627
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | lower | 2050 | 0.32541
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N | 2, 4 | upper | 2050 | 0.53424
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2040
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2015
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2040
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | ctrl | 2015 | 0.005
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | ctrl | 2020 | 0.004
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | ctrl | 2030 | 0.003
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | ctrl | 2040 | 0.003
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | ctrl | 2050 | 0.003
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | ctrl | 2015 | 950.5924
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | ctrl | 2020 | 1010.328
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | ctrl | 2030 | 1116.06
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | ctrl | 2040 | 1127.808
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | ctrl | 2050 | 1139.556
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1,I |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2015 | 1045.6516
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2020 | 1111.3608
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2030 | 1227.666
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2040 | 1240.5888
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2050 | 1253.5116
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | ctrl | 2015 | 13000
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | ctrl | 2020 | 9600
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | lower | 2020 | 8600
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | upper | 2020 | 10600
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | ctrl | 2030 | 8100
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | ctrl | 2040 | 7300
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | ctrl | 2050 | 6800
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | lower | 2050 | 6100
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 | P |  | upper | 2050 | 7500
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2015
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2030
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2040
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2015 | 13000
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2020 | 9600
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2030 | 8100
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2040 | 7300
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2050 | 6800
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B2,C |  | ctrl | 2015 | 0.11
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B2,C |  | ctrl | 2020 | 0.11
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B2,C |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B2,C |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B2,C |  | ctrl | 2030 | 0.11
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B2,C |  | ctrl | 2040 | 0.11
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B2,C |  | ctrl | 2050 | 0.11
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B2,C |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | B2,C |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2015 | 1068
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2020 | 1068
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2030 | 1068
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2040 | 1068
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2050 | 1068
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2015 | 10
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2020 | 12.5
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2030 | 15
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2040 | 15
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2050 | 15
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.043616
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.042876
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.046203
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.035138
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.031542
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.029781
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.027284
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.03347
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.17446
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.17151
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.18481
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.11323
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.091243
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.081337
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.069449
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.096983
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | ctrl | 2015 | 0.8136
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | ctrl | 2020 | 0.43616
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | lower | 2020 | 0.42876
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | upper | 2020 | 0.46203
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | ctrl | 2030 | 0.24174
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | ctrl | 2040 | 0.18002
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | ctrl | 2050 | 0.15388
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | lower | 2050 | 0.1248
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 | M,O |  | upper | 2050 | 0.28986
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.11895
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.11694
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.12601
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.095831
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.086024
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.08122
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.074411
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.091281
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.1586
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.15591
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.16801
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.10294
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.082948
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.073943
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.063135
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.088166
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.55797
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.079301
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.077957
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.084005
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.063888
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.057349
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.054147
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.049608
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.060854
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.61377
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.087231
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.085753
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.092406
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.070276
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.063084
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.059561
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.054568
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.066939
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | ctrl | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | ctrl | 2030
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | ctrl | 2040
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | ctrl | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 |  |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | ctrl | 2015 | 0.73963
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | ctrl | 2020 | 0.39651
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | lower | 2020 | 0.38978
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | upper | 2020 | 0.42003
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | ctrl | 2030 | 0.21977
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | ctrl | 2040 | 0.16366
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | ctrl | 2050 | 0.13989
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | lower | 2050 | 0.11345
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 | M,O |  | upper | 2050 | 0.26351
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.039651
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.038978
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.042003
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.031944
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.028675
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.027073
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.024804
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.030427
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2015 | 0.165
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2020 | 0.205
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2030 | 0.23
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2040 | 0.245
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2050 | 0.26
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | ctrl | 2015 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | ctrl | 2020 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | ctrl | 2030 | 0
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | ctrl | 2040 | 0.01
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | ctrl | 2050 | 0.02
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  |  | 3 | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2015 | 0.81
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2020 | 0.86
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2030 | 0.95
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2040 | 0.96
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2050 | 0.97
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2015 | 1.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2020 | 1.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2030 | 1.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2040 | 1.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2050 | 1.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | W | 6 | ctrl | 2015 | 6.0606
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | W | 6 | ctrl | 2020 | 4.878
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | W | 6 | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | W | 6 | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | W | 6 | ctrl | 2030 | 4.3478
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | W | 6 | ctrl | 2040 | 4.0816
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | W | 6 | ctrl | 2050 | 3.8462
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | W | 6 | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | W | 6 | upper | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2015 | 1.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2020 | 1.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | lower | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | upper | 2020
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2030 | 1.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2040 | 1.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2050 | 1.1
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | lower | 2050
22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015 | 0.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 0.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 0.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2040 | 0.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 0.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2040 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015 | 4
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2040 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2040 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | ctrl | 2015 | 20.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | ctrl | 2020 | 13.75
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | ctrl | 2030 | 12.2554
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | ctrl | 2040 | 11.5051
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | ctrl | 2050 | 10.8413
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2015 | 30
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2020 | 35
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2030 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2040 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2050 | 40
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 |  |  | ctrl | 2015 | 13600
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 |  |  | ctrl | 2020 | 11300
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 |  |  | lower | 2020 | 10100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 |  |  | upper | 2020 | 12400
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 |  |  | ctrl | 2030 | 9500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 |  |  | ctrl | 2040 | 8100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 |  |  | ctrl | 2050 | 7400
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 |  |  | lower | 2050 | 6600
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 |  |  | upper | 2050 | 8100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | ctrl | 2015
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | ctrl | 2020 | 4400
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | ctrl | 2030 | 3900
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | ctrl | 2040 | 3100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | ctrl | 2050 | 2500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2015 | 1.5481
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2020 | 0.5625
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2020 | 0.54375
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2020 | 0.6
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2030 | 0.38373
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2040 | 0.32082
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2050 | 0.29258
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2050 | 0.25332
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2050 | 0.40023
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2015 | 1.1467
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2020 | 0.45
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2020 | 0.435
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2020 | 0.48
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2030 | 0.30698
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2040 | 0.25666
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2050 | 0.23406
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2050 | 0.20266
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2050 | 0.32019
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2015
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2030
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2040
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2015
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2030
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2040
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | ctrl | 2015 | 0.005
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | ctrl | 2020 | 0.004
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | lower | 2020 | 0.003
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | upper | 2020 | 0.005
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | ctrl | 2030 | 0.003
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | ctrl | 2040 | 0.003
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | ctrl | 2050 | 0.003
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | ctrl | 2015 | 981.3318
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | ctrl | 2020 | 1074.6216
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | ctrl | 2030 | 1187.082
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | ctrl | 2040 | 1199.5776
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | ctrl | 2050 | 1212.0732
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2015 | 1324.7979
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2020 | 1343.277
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2030 | 1483.8525
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2040 | 1499.472
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2050 | 1515.0915
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2015 | 10100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2020 | 9000
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2020 | 8100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2020 | 9900
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2030 | 7600
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2040 | 6500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2050 | 5900
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2050 | 5300
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2050 | 6500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2015
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2020 | 3500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2030 | 3100
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2040 | 2500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2050 | 2000
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2015
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2020 | 5500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2030 | 4500
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2040 | 4000
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2050 | 3900
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | ctrl | 2015 | 5.4
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | ctrl | 2020 | 50
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | ctrl | 2030 | 50
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | ctrl | 2040 | 50
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | ctrl | 2050 | 50
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2015 | 1068
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2020 | 1068
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2030 | 1068
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2040 | 1068
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2050 | 1068
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2015 | 10
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2020 | 12.5
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2030 | 15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2040 | 15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2050 | 15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.086006
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.061141
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.059103
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.065217
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.049258
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.044216
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.041747
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.03761
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.047244
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.11467
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.031207
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.030166
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.033287
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.020254
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.016321
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.014549
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.012215
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.017468
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.88873
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.25679
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.24823
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.27391
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.14233
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.10599
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.0906
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.072253
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.17066
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2015 | 0.10618
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.10221
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.098802
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.10902
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.082343
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.073916
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.069788
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.062872
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.078977
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.084944
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.024965
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.024133
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.02663
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.016204
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.013057
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.011639
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.0097724
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.013974
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.16989
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.03913
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.037826
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.041739
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.031525
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.028298
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.026718
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.02407
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.030236
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.22935
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.048913
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.047283
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.052174
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.039406
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.035373
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.033398
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.030088
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.037795
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | ctrl | 2015 | 0.086006
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.036685
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.035462
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.03913
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.029555
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.02653
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.025048
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.022566
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.028346
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015 | 0.65832
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.20543
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.19859
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.21913
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.11386
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.084792
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.07248
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.057802
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.13653
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2015 | 0.063708
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.029348
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.02837
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.031304
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.023644
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.021224
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.020039
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.018053
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.022677
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | ctrl | 2015 | 0.063708
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | ctrl | 2020 | 0.048913
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | lower | 2020 | 0.047283
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | upper | 2020 | 0.052174
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | ctrl | 2030 | 0.039406
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | ctrl | 2040 | 0.035373
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | ctrl | 2050 | 0.033398
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | lower | 2050 | 0.030088
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | upper | 2050 | 0.037795
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2015 | 0.165
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2020 | 0.205
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | lower | 2020 | 0.2
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | upper | 2020 | 0.21
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2030 | 0.23
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2040 | 0.245
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2050 | 0.26
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | ctrl | 2015 | 0
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | ctrl | 2020 | 0.01
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | ctrl | 2030 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | ctrl | 2040 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | ctrl | 2050 | 0.05
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2015 | 0.81
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2020 | 0.86
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2030 | 0.95
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2040 | 0.96
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2050 | 0.97
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2015 | 1.35
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2020 | 1.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2030 | 1.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2040 | 1.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | ctrl | 2050 | 1.25
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 6 | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2015 | 15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2020 | 11
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2030 | 9.8043
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2040 | 9.2041
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2050 | 8.6731
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | upper | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2015 | 1.15
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2020 | 1.17
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | lower | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | upper | 2020
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2030 | 1.17
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2040 | 1.17
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2050 | 1.17
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | lower | 2050
22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 0.5
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 0.5
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2040 | 0.5
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 0.5
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2040 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2040 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2040 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 0
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | ctrl | 2020 | 17.875
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | ctrl | 2030 | 15.9321
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | ctrl | 2040 | 14.9566
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | ctrl | 2050 | 14.0938
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | B,B1 | 6 | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2020 | 35
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2030 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2040 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2050 | 40
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2020 | 12100
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P2 |  | lower | 2020 | 10900
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P2 |  | upper | 2020 | 13400
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2030 | 10400
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2040 | 9400
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2050 | 9000
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P2 |  | lower | 2050 | 8100
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | P2 |  | upper | 2050 | 9900
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | ctrl | 2020 | 5300
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | ctrl | 2030 | 4800
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | ctrl | 2040 | 4400
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | ctrl | 2050 | 4100
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Fixed O&M (land rent) [2020-EUR/MW_e/y] | Fixed O&M | land rent | EUR/MW_e/y | 2020 | S |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2020 | 0.65035
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2020 | 0.59726
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2020 | 0.70344
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2030 | 0.45447
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2040 | 0.38431
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2050 | 0.35251
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2050 | 0.29196
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2050 | 0.47227
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2020 | 0.52028
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2020 | 0.47781
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2020 | 0.56275
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2030 | 0.36358
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2040 | 0.30745
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2050 | 0.28201
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | lower | 2050 | 0.23357
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total, per DC) [2020-MEUR/MW_e] | Nominal investment | *total, per DC | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | upper | 2050 | 0.37782
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2030
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2040
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2030
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2040
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | ctrl | 2020 | 0.004
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | lower | 2020 | 0.003
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | upper | 2020 | 0.005
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | ctrl | 2030 | 0.003
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | ctrl | 2040 | 0.003
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | ctrl | 2050 | 0.003
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual degradation of full-load hours [] | Average annual degradation of full-load hours |  | [] |  | A2 |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | ctrl | 2020 | 1235.8148
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | ctrl | 2030 | 1369.71
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | ctrl | 2040 | 1379.5142
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | ctrl | 2050 | 1393.8842
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours (DC-value) [MWh_e/MW_e] | Average annual full-load hours | DC-value | MWh_e/MW_e |  | A1, K |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2020 | 1544.7686
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2030 | 1712.1375
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2040 | 1724.3928
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | ctrl | 2050 | 1742.3552
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | A1 |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2020 | 9700
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2020 | 8700
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2020 | 10700
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2030 | 8300
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2040 | 7500
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | ctrl | 2050 | 7200
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | lower | 2050 | 6500
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | Fixed O&M | *total, per DC | EUR/MW_e/y | 2020 |  |  | upper | 2050 | 7900
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2020 | 4200
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2030 | 3800
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2040 | 3500
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | ctrl | 2050 | 3300
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | Fixed O&M | land rent, per DC | EUR/MW_e/y | 2020 | S | 6 | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2020 | 5500
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2030 | 4500
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2040 | 4000
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | ctrl | 2050 | 3900
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | Fixed O&M | other, per DC | EUR/MW_e/y | 2020 | P2 |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | ctrl | 2020 | 50
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | ctrl | 2030 | 50
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | ctrl | 2040 | 50
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | ctrl | 2050 | 50
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Generating capacity for one unit (DC-value) [MW_e] | Generating capacity for one unit | DC-value | MW_e |  | C |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2020 | 1068
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2030 | 1068
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2040 | 1068
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | ctrl | 2050 | 1068
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Global horizontal irradiance [MWh/m2/y] | Global horizontal irradiance |  | MWh/m2/y |  | A | 1 | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2020 | 12.5
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2030 | 15
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2040 | 15
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | ctrl | 2050 | 15
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Inverter lifetime [years] | Inverter lifetime |  | years |  |  | 6 | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.061174
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.056181
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.066168
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.049284
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.04424
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.04177
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.03575
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.047933
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.031223
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.028675
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.033772
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.020265
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.01633
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.014557
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.011611
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (inverter) [2020-MEUR/MW_e] | Nominal investment | inverter | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.017723
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.25693
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.23596
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.27791
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.14241
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.10605
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.090649
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.06868
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (pv modules) [2020-MEUR/MW_e] | Nominal investment | pv modules | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.17075
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [2020-MEUR/MW_e] | Nominal investment | tracker related costs | MEUR/MW_e | 2020 | T |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [2020-MEUR/MW_e] | Nominal investment | tracker related costs | MEUR/MW_e | 2020 | T |  | ctrl | 2020 | 0.087547
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [2020-MEUR/MW_e] | Nominal investment | tracker related costs | MEUR/MW_e | 2020 | T |  | lower | 2020 | 0.080401
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [2020-MEUR/MW_e] | Nominal investment | tracker related costs | MEUR/MW_e | 2020 | T |  | upper | 2020 | 0.094694
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [2020-MEUR/MW_e] | Nominal investment | tracker related costs | MEUR/MW_e | 2020 | T |  | ctrl | 2030 | 0.070531
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [2020-MEUR/MW_e] | Nominal investment | tracker related costs | MEUR/MW_e | 2020 | T |  | ctrl | 2040 | 0.063313
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [2020-MEUR/MW_e] | Nominal investment | tracker related costs | MEUR/MW_e | 2020 | T |  | ctrl | 2050 | 0.059777
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [2020-MEUR/MW_e] | Nominal investment | tracker related costs | MEUR/MW_e | 2020 | T |  | lower | 2050 | 0.051163
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (tracker related costs) [2020-MEUR/MW_e] | Nominal investment | tracker related costs | MEUR/MW_e | 2020 | T |  | upper | 2050 | 0.068597
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.10226
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.093916
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.11061
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.082387
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.073956
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.069826
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.059763
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (installation, per DC) [2020-MEUR/MW_e] | Nominal investment | installation, per DC | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.080128
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.024979
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.02294
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.027018
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.016212
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.013064
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.011645
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.0092891
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | Nominal investment | inverter, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.014178
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.029364
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.026967
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.031761
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.023656
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.021235
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.02005
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.01716
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.023008
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.036705
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.033708
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.039701
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.029571
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.026544
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.025062
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.02145
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | Nominal investment | other, i.e. residual balance of plant | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.02876
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.04894
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.044944
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.052935
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.039427
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.035392
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.033416
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.0286
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (soft costs) [2020-MEUR/MW_e] | Nominal investment | soft costs | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.038346
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2020 | 0.20555
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | lower | 2020 | 0.18877
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | upper | 2020 | 0.22233
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2030 | 0.11393
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2040 | 0.084838
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | ctrl | 2050 | 0.072519
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | lower | 2050 | 0.054944
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | Nominal investment | pv module, per DC | MEUR/MW_e | 2020 |  |  | upper | 2050 | 0.1366
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2020 | 0.039152
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | lower | 2020 | 0.035956
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | upper | 2020 | 0.042348
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2030 | 0.031542
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2040 | 0.028314
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | ctrl | 2050 | 0.026733
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | lower | 2050 | 0.02288
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | Nominal investment | soft costs, per DC | MEUR/MW_e | 2020 | V |  | upper | 2050 | 0.030677
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] | Nominal investment | tracker related cost, per DC | MEUR/MW_e | 2020 | T |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] | Nominal investment | tracker related cost, per DC | MEUR/MW_e | 2020 | T |  | ctrl | 2020 | 0.070038
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] | Nominal investment | tracker related cost, per DC | MEUR/MW_e | 2020 | T |  | lower | 2020 | 0.064321
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] | Nominal investment | tracker related cost, per DC | MEUR/MW_e | 2020 | T |  | upper | 2020 | 0.075755
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] | Nominal investment | tracker related cost, per DC | MEUR/MW_e | 2020 | T |  | ctrl | 2030 | 0.056425
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] | Nominal investment | tracker related cost, per DC | MEUR/MW_e | 2020 | T |  | ctrl | 2040 | 0.05065
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] | Nominal investment | tracker related cost, per DC | MEUR/MW_e | 2020 | T |  | ctrl | 2050 | 0.047822
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] | Nominal investment | tracker related cost, per DC | MEUR/MW_e | 2020 | T |  | lower | 2050 | 0.04093
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] | Nominal investment | tracker related cost, per DC | MEUR/MW_e | 2020 | T |  | upper | 2050 | 0.054878
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | ctrl | 2020 | 0.04894
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | lower | 2020 | 0.044944
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | upper | 2020 | 0.052935
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | ctrl | 2030 | 0.039427
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | ctrl | 2040 | 0.035392
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | ctrl | 2050 | 0.033416
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | lower | 2050 | 0.0286
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | Nominal investment | transformer and grid connection, per DC | MEUR/MW_e | 2020 | R |  | upper | 2050 | 0.038346
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2020 | 0.205
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | lower | 2020 | 0.2
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | upper | 2020 | 0.21
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2030 | 0.23
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2040 | 0.245
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | ctrl | 2050 | 0.26
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | PV module conversion efficiency [] | PV module conversion efficiency |  | [] |  | U | 3 | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | ctrl | 2020 | 0.01
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | ctrl | 2030 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | ctrl | 2040 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | ctrl | 2050 | 0.05
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (contribution from bifaciality) [] | Performance ratio | contribution from bifaciality | [] |  | H | 3 | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2020 | 0.86
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2030 | 0.95
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2040 | 0.96
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | ctrl | 2050 | 0.97
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Performance ratio (measure of combined losses) [] | Performance ratio | measure of combined losses | [] |  | F |  | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 5, 6 | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 5, 6 | ctrl | 2020 | 1.25
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 5, 6 | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 5, 6 | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 5, 6 | ctrl | 2030 | 1.25
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 5, 6 | ctrl | 2040 | 1.25
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 5, 6 | ctrl | 2050 | 1.25
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 5, 6 | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Sizing factor (DC/AC) [W_e/W_e] | Sizing factor | DC/AC | W_e/W_e |  | D | 5, 6 | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2020 | 14.3
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2030 | 12.7457
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2040 | 11.9653
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | ctrl | 2050 | 11.275
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Space requirement (per DC) [1000m2/MW_e] | Space requirement | per DC | 1000m2/MW_e |  | B,B1 | 6 | upper | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2015
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2020 | 1.3455
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | lower | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | upper | 2020
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2030 | 1.35
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2040 | 1.3455
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | ctrl | 2050 | 1.3455
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | lower | 2050
22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Technology-specific data | Transposition factor | Transposition factor |  |  |  | E |  | upper | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E, F, M | 1 | ctrl | 2020 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E, F, M | 1 | ctrl | 2025 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E, F, M | 1 | lower | 2025 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E, F, M | 1 | upper | 2025 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E, F, M | 1 | ctrl | 2030 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E, F, M | 1 | ctrl | 2040 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E, F, M | 1 | ctrl | 2050 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E, F, M | 1 | lower | 2050 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E, F, M | 1 | upper | 2050 | 0.029
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | H, I, M | 1 | ctrl | 2020 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | H, I, M | 1 | ctrl | 2025 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | H, I, M | 1 | lower | 2025 | 1.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | H, I, M | 1 | upper | 2025 | 3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | H, I, M | 1 | ctrl | 2030 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | H, I, M | 1 | ctrl | 2040 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | H, I, M | 1 | ctrl | 2050 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | H, I, M | 1 | lower | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | H, I, M | 1 | upper | 2050 | 3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | M | 1 | ctrl | 2020 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | M | 1 | ctrl | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | M | 1 | lower | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | M | 1 | upper | 2025 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | M | 1 | ctrl | 2030 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | M | 1 | ctrl | 2040 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | M | 1 | ctrl | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | M | 1 | lower | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | M | 1 | upper | 2050 | 0.05
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A,B, M | 1 | ctrl | 2020 | 65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A,B, M | 1 | ctrl | 2025 | 65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A,B, M | 1 | lower | 2025 | 30
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A,B, M | 1 | upper | 2025 | 150
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A,B, M | 1 | ctrl | 2030 | 65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A,B, M | 1 | ctrl | 2040 | 65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A,B, M | 1 | ctrl | 2050 | 65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A,B, M | 1 | lower | 2050 | 30
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A,B, M | 1 | upper | 2050 | 300
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | M | 1 | ctrl | 2020 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | M | 1 | ctrl | 2025 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | M | 1 | lower | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | M | 1 | upper | 2025 | 4
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | M | 1 | ctrl | 2030 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | M | 1 | ctrl | 2040 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | M | 1 | ctrl | 2050 | 2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | M | 1 | lower | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | M | 1 | upper | 2050 | 4
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | M | 1 | ctrl | 2020 | 0.025385
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | M | 1 | ctrl | 2025 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | M | 1 | lower | 2025 | 0.02
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | M | 1 | upper | 2025 | 0.06
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | M | 1 | ctrl | 2030 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | M | 1 | ctrl | 2040 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | M | 1 | ctrl | 2050 | 0.03
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | M | 1 | lower | 2050 | 0.02
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | M | 1 | upper | 2050 | 0.06
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | G,M | 1 | ctrl | 2020 | 25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | G,M | 1 | ctrl | 2025 | 25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | G,M | 1 | lower | 2025 | 15
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | G,M | 1 | upper | 2025 | 40
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | G,M | 1 | ctrl | 2030 | 25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | G,M | 1 | ctrl | 2040 | 25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | G,M | 1 | ctrl | 2050 | 25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | G,M | 1 | lower | 2050 | 15
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | G,M | 1 | upper | 2050 | 40
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | C, D, F, M, V | 1 | ctrl | 2020 | 3.01
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | C, D, F, M, V | 1 | ctrl | 2025 | 3.01
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | C, D, F, M, V | 1 | lower | 2025 | 2.9
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | C, D, F, M, V | 1 | upper | 2025 | 3.1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | C, D, F, M, V | 1 | ctrl | 2030 | 3.01
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | C, D, F, M, V | 1 | ctrl | 2040 | 3.11
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | C, D, F, M, V | 1 | ctrl | 2050 | 3.11
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | C, D, F, M, V | 1 | lower | 2050 | 3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | C, D, F, M, V | 1 | upper | 2050 | 3.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | C, D, F, M | 1 | ctrl | 2020 | 3.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | C, D, F, M | 1 | ctrl | 2025 | 3.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | C, D, F, M | 1 | lower | 2025 | 3.1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | C, D, F, M | 1 | upper | 2025 | 3.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | C, D, F, M | 1 | ctrl | 2030 | 3.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | C, D, F, M | 1 | ctrl | 2040 | 3.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | C, D, F, M | 1 | ctrl | 2050 | 3.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | C, D, F, M | 1 | lower | 2050 | 3.2
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | C, D, F, M | 1 | upper | 2050 | 3.4
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | M, R | 1 | ctrl | 2020 | 2047.3532
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | M, R | 1 | ctrl | 2025 | 2047.3532
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | M, R | 1 | lower | 2025 | 1485.15
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | M, R | 1 | upper | 2025 | 2970.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | M, R | 1 | ctrl | 2030 | 2047.3532
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | M, R | 1 | ctrl | 2040 | 2047.3532
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | M, R | 1 | ctrl | 2050 | 2047.3532
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | M, R | 1 | lower | 2050 | 1485.15
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | M, R | 1 | upper | 2050 | 2970.3
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2020 | 0.93564
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2025 | 0.93564
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | A, M, R | 1 | lower | 2025 | 0.79208
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | A, M, R | 1 | upper | 2025 | 1.4035
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2030 | 0.88886
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2040 | 0.84208
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2050 | 0.79529
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | A, M, R | 1 | lower | 2050 | 0.65495
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | A, M, R | 1 | upper | 2050 | 1.4035
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (seawater system) [2020-MEUR/MW_h] | Nominal investment | seawater system | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2020 | 0.20269
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (seawater system) [2020-MEUR/MW_h] | Nominal investment | seawater system | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2025 | 0.20269
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (seawater system) [2020-MEUR/MW_h] | Nominal investment | seawater system | MEUR/MW_h | 2020 | M, R | 1 | lower | 2025 | 0.14852
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (seawater system) [2020-MEUR/MW_h] | Nominal investment | seawater system | MEUR/MW_h | 2020 | M, R | 1 | upper | 2025 | 0.30403
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (seawater system) [2020-MEUR/MW_h] | Nominal investment | seawater system | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2030 | 0.19255
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (seawater system) [2020-MEUR/MW_h] | Nominal investment | seawater system | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2040 | 0.18242
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (seawater system) [2020-MEUR/MW_h] | Nominal investment | seawater system | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2050 | 0.17228
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (seawater system) [2020-MEUR/MW_h] | Nominal investment | seawater system | MEUR/MW_h | 2020 | M, R | 1 | lower | 2050 | 0.14188
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (seawater system) [2020-MEUR/MW_h] | Nominal investment | seawater system | MEUR/MW_h | 2020 | M, R | 1 | upper | 2050 | 0.30403
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2020-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2020 | 0.57326
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2020-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2025 | 0.57326
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2020-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2020 | M, R | 1 | lower | 2025 | 0.44555
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2020-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2020 | M, R | 1 | upper | 2025 | 0.85989
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2020-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2030 | 0.5446
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2020-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2040 | 0.51593
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2020-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2050 | 0.48727
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2020-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2020 | M, R | 1 | lower | 2050 | 0.40128
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2020-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2020 | M, R | 1 | upper | 2050 | 0.85989
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2020 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2020 | M, R | 1 | lower | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2020 | M, R | 1 | upper | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2030 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2040 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2020 | M, R | 1 | lower | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2020 | M, R | 1 | upper | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (other) [2020-MEUR/MW_h] | Nominal investment | other | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2020 | 0.15969
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (other) [2020-MEUR/MW_h] | Nominal investment | other | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2025 | 0.15969
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (other) [2020-MEUR/MW_h] | Nominal investment | other | MEUR/MW_h | 2020 | M, R | 1 | lower | 2025 | 0.12871
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (other) [2020-MEUR/MW_h] | Nominal investment | other | MEUR/MW_h | 2020 | M, R | 1 | upper | 2025 | 0.23954
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (other) [2020-MEUR/MW_h] | Nominal investment | other | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2030 | 0.15171
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (other) [2020-MEUR/MW_h] | Nominal investment | other | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2040 | 0.14372
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (other) [2020-MEUR/MW_h] | Nominal investment | other | MEUR/MW_h | 2020 | M, R | 1 | ctrl | 2050 | 0.13574
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (other) [2020-MEUR/MW_h] | Nominal investment | other | MEUR/MW_h | 2020 | M, R | 1 | lower | 2050 | 0.11179
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (other) [2020-MEUR/MW_h] | Nominal investment | other | MEUR/MW_h | 2020 | M, R | 1 | upper | 2050 | 0.23954
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 | M, Q | 1 | ctrl | 2020 | 4.9505
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 | M, Q | 1 | ctrl | 2025 | 4.9505
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 | M, Q | 1 | lower | 2025 | 2.9703
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 | M, Q | 1 | upper | 2025 | 14.8515
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 | M, Q | 1 | ctrl | 2030 | 4.9505
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 | M, Q | 1 | ctrl | 2040 | 4.9505
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 | M, Q | 1 | ctrl | 2050 | 4.9505
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 | M, Q | 1 | lower | 2050 | 2.9703
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 | M, Q | 1 | upper | 2050 | 14.8515
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2020 | 0.9901
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2025 | 0.9901
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | M, R, S | 1 | lower | 2025 | 0.49505
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | M, R, S | 1 | upper | 2025 | 1.9802
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2030 | 0.9901
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2040 | 0.9901
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2050 | 0.9901
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | M, R, S | 1 | lower | 2050 | 0.49505
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | M, R, S | 1 | upper | 2050 | 1.9802
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M, P | 1 | ctrl | 2020 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M, P | 1 | ctrl | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M, P | 1 | lower | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M, P | 1 | upper | 2025 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M, P | 1 | ctrl | 2030 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M, P | 1 | ctrl | 2040 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M, P | 1 | ctrl | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M, P | 1 | lower | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M, P | 1 | upper | 2050 | 0
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2020 | 0.9901
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2025 | 0.9901
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | M, R, S | 1 | lower | 2025 | 0.49505
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | M, R, S | 1 | upper | 2025 | 1.9802
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2030 | 0.9901
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2040 | 0.9901
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | M, R, S | 1 | ctrl | 2050 | 0.9901
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | M, R, S | 1 | lower | 2050 | 0.49505
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | M, R, S | 1 | upper | 2050 | 1.9802
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | K, O, M | 1 | ctrl | 2020 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | K, O, M | 1 | ctrl | 2025 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | K, O, M | 1 | lower | 2025 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | K, O, M | 1 | upper | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | K, O, M | 1 | ctrl | 2030 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | K, O, M | 1 | ctrl | 2040 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | K, O, M | 1 | ctrl | 2050 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | K, O, M | 1 | lower | 2050 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | K, O, M | 1 | upper | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | K, L, M | 1 | ctrl | 2020 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | K, L, M | 1 | ctrl | 2025 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | K, L, M | 1 | lower | 2025 | 0.1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | K, L, M | 1 | upper | 2025 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | K, L, M | 1 | ctrl | 2030 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | K, L, M | 1 | ctrl | 2040 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | K, L, M | 1 | ctrl | 2050 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | K, L, M | 1 | lower | 2050 | 0.1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | K, L, M | 1 | upper | 2050 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J, K, M | 1 | ctrl | 2020 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J, K, M | 1 | ctrl | 2025 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J, K, M | 1 | lower | 2025 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J, K, M | 1 | upper | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J, K, M | 1 | ctrl | 2030 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J, K, M | 1 | ctrl | 2040 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J, K, M | 1 | ctrl | 2050 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J, K, M | 1 | lower | 2050 | 0.65
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J, K, M | 1 | upper | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | J, K, M | 1 | ctrl | 2020 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | J, K, M | 1 | ctrl | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | J, K, M | 1 | lower | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | J, K, M | 1 | upper | 2025 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | J, K, M | 1 | ctrl | 2030 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | J, K, M | 1 | ctrl | 2040 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | J, K, M | 1 | ctrl | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | J, K, M | 1 | lower | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | J, K, M | 1 | upper | 2050 | 1
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | K, N, M | 1 | ctrl | 2020 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | K, N, M | 1 | ctrl | 2025 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | K, N, M | 1 | lower | 2025 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | K, N, M | 1 | upper | 2025 | 0.75
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | K, N, M | 1 | ctrl | 2030 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | K, N, M | 1 | ctrl | 2040 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | K, N, M | 1 | ctrl | 2050 | 0.5
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | K, N, M | 1 | lower | 2050 | 0.25
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | K, N, M | 1 | upper | 2050 | 0.75
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (grid connection fee) [2020-MEUR/MW_h] | Nominal investment | grid connection fee | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2020 | 0.051184
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (grid connection fee) [2020-MEUR/MW_h] | Nominal investment | grid connection fee | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2025 | 0.051184
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (grid connection fee) [2020-MEUR/MW_h] | Nominal investment | grid connection fee | MEUR/MW_h | 2020 | M, T | 1 | lower | 2025 | 0.012182
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (grid connection fee) [2020-MEUR/MW_h] | Nominal investment | grid connection fee | MEUR/MW_h | 2020 | M, T | 1 | upper | 2025 | 0.076776
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (grid connection fee) [2020-MEUR/MW_h] | Nominal investment | grid connection fee | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2030 | 0.048625
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (grid connection fee) [2020-MEUR/MW_h] | Nominal investment | grid connection fee | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2040 | 0.046065
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (grid connection fee) [2020-MEUR/MW_h] | Nominal investment | grid connection fee | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2050 | 0.043506
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (grid connection fee) [2020-MEUR/MW_h] | Nominal investment | grid connection fee | MEUR/MW_h | 2020 | M, T | 1 | lower | 2050 | 0.025592
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (grid connection fee) [2020-MEUR/MW_h] | Nominal investment | grid connection fee | MEUR/MW_h | 2020 | M, T | 1 | upper | 2050 | 0.076776
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (heatpump building) [2020-MEUR/MW_h] | Nominal investment | heatpump building | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2020 | 0.10851
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (heatpump building) [2020-MEUR/MW_h] | Nominal investment | heatpump building | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2025 | 0.10851
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (heatpump building) [2020-MEUR/MW_h] | Nominal investment | heatpump building | MEUR/MW_h | 2020 | M, T | 1 | lower | 2025 | 0.092233
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (heatpump building) [2020-MEUR/MW_h] | Nominal investment | heatpump building | MEUR/MW_h | 2020 | M, T | 1 | upper | 2025 | 0.16276
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (heatpump building) [2020-MEUR/MW_h] | Nominal investment | heatpump building | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2030 | 0.10308
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (heatpump building) [2020-MEUR/MW_h] | Nominal investment | heatpump building | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2040 | 0.097659
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (heatpump building) [2020-MEUR/MW_h] | Nominal investment | heatpump building | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2050 | 0.092233
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (heatpump building) [2020-MEUR/MW_h] | Nominal investment | heatpump building | MEUR/MW_h | 2020 | M, T | 1 | lower | 2050 | 0.054255
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (heatpump building) [2020-MEUR/MW_h] | Nominal investment | heatpump building | MEUR/MW_h | 2020 | M, T | 1 | upper | 2050 | 0.16276
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater connection) [2020-MEUR/MW_h] | Nominal investment | seawater connection | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2020 | 0.083941
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater connection) [2020-MEUR/MW_h] | Nominal investment | seawater connection | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2025 | 0.083941
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater connection) [2020-MEUR/MW_h] | Nominal investment | seawater connection | MEUR/MW_h | 2020 | M, T | 1 | lower | 2025 | 0.07135
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater connection) [2020-MEUR/MW_h] | Nominal investment | seawater connection | MEUR/MW_h | 2020 | M, T | 1 | upper | 2025 | 0.12591
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater connection) [2020-MEUR/MW_h] | Nominal investment | seawater connection | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2030 | 0.079744
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater connection) [2020-MEUR/MW_h] | Nominal investment | seawater connection | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2040 | 0.075547
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater connection) [2020-MEUR/MW_h] | Nominal investment | seawater connection | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2050 | 0.07135
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater connection) [2020-MEUR/MW_h] | Nominal investment | seawater connection | MEUR/MW_h | 2020 | M, T | 1 | lower | 2050 | 0.041971
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater connection) [2020-MEUR/MW_h] | Nominal investment | seawater connection | MEUR/MW_h | 2020 | M, T | 1 | upper | 2050 | 0.12591
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater intake) [2020-MEUR/MW_h] | Nominal investment | seawater intake | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2020 | 0.053231
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater intake) [2020-MEUR/MW_h] | Nominal investment | seawater intake | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2025 | 0.053231
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater intake) [2020-MEUR/MW_h] | Nominal investment | seawater intake | MEUR/MW_h | 2020 | M, T | 1 | lower | 2025 | 0.045247
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater intake) [2020-MEUR/MW_h] | Nominal investment | seawater intake | MEUR/MW_h | 2020 | M, T | 1 | upper | 2025 | 0.079847
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater intake) [2020-MEUR/MW_h] | Nominal investment | seawater intake | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2030 | 0.05057
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater intake) [2020-MEUR/MW_h] | Nominal investment | seawater intake | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2040 | 0.047908
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater intake) [2020-MEUR/MW_h] | Nominal investment | seawater intake | MEUR/MW_h | 2020 | M, T | 1 | ctrl | 2050 | 0.045247
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater intake) [2020-MEUR/MW_h] | Nominal investment | seawater intake | MEUR/MW_h | 2020 | M, T | 1 | lower | 2050 | 0.026616
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater intake) [2020-MEUR/MW_h] | Nominal investment | seawater intake | MEUR/MW_h | 2020 | M, T | 1 | upper | 2050 | 0.079847
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater piping) [2020-EUR/m] | Nominal investment | seawater piping | EUR/m | 2020 | M, T | 1 | ctrl | 2020 | 1663.4745
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater piping) [2020-EUR/m] | Nominal investment | seawater piping | EUR/m | 2020 | M, T | 1 | ctrl | 2025 | 1663.4745
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater piping) [2020-EUR/m] | Nominal investment | seawater piping | EUR/m | 2020 | M, T | 1 | lower | 2025 | 1413.9533
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater piping) [2020-EUR/m] | Nominal investment | seawater piping | EUR/m | 2020 | M, T | 1 | upper | 2025 | 2495.2117
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater piping) [2020-EUR/m] | Nominal investment | seawater piping | EUR/m | 2020 | M, T | 1 | ctrl | 2030 | 1580.3007
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater piping) [2020-EUR/m] | Nominal investment | seawater piping | EUR/m | 2020 | M, T | 1 | ctrl | 2040 | 1497.127
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater piping) [2020-EUR/m] | Nominal investment | seawater piping | EUR/m | 2020 | M, T | 1 | ctrl | 2050 | 1413.9533
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater piping) [2020-EUR/m] | Nominal investment | seawater piping | EUR/m | 2020 | M, T | 1 | lower | 2050 | 831.7372
40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Technology-specific data | Nominal investment (seawater piping) [2020-EUR/m] | Nominal investment | seawater piping | EUR/m | 2020 | M, T | 1 | upper | 2050 | 2495.2117
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | 2, 3; 4 | ctrl | 2020 | 0.096257
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | 2, 3; 4 | ctrl | 2025 | 0.096257
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | 2, 3; 4 | lower | 2025 | 0.096257
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | 2, 3; 4 | upper | 2025 | 0.096257
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | 2, 3; 4 | ctrl | 2030 | 0.096257
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | 2, 3; 4 | ctrl | 2040 | 0.095
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | 2, 3; 4 | ctrl | 2050 | 0.094
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | 2, 3; 4 | lower | 2050 | 0.096257
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | 2, 3; 4 | upper | 2050 | 0.094
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2020 | 4.5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2025 | 4.5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2025 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2025 | 5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2030 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2040 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2050 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2050 | 3
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2050 | 5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2020 | 0.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2025 | 0.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2025 | 0.01
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2025 | 0.03
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2030 | 0.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2040 | 0.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2050 | 0.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2050 | 0.01
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2050 | 0.03
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | I,A | 1, 2 | ctrl | 2020 | 121
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | I,A | 1, 2 | ctrl | 2025 | 120.769
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | I,A | 1, 2 | lower | 2025 | 120.769
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | I,A | 1, 2 | upper | 2025 | 120.769
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | I,A | 1, 2 | ctrl | 2030 | 120.3844
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | I,A | 1, 2 | ctrl | 2040 | 119.6692
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | I,A | 1, 2 | ctrl | 2050 | 119.3241
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | I,A | 1, 2 | lower | 2050 | 119.3241
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | I,A | 1, 2 | upper | 2050 | 119.3241
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2020 | 2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2025 | 2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2025 | 1
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2025 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2030 | 2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2040 | 2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2050 | 2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2050 | 1
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2050 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2025 | 3
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2025 | 7
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2050 | 3
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2050 | 7
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2020 | 25
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2025 | 25
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2025 | 25
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2025 | 30
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2030 | 30
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2040 | 30
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2050 | 30
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2050 | 25
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2050 | 35
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | A,G |  | ctrl | 2020 | 3.74
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | A,G |  | ctrl | 2025 | 3.74
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | A,G |  | lower | 2025 | 3.74
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | A,G |  | upper | 2025 | 3.74
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | A,G |  | ctrl | 2030 | 3.74
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | A,G |  | ctrl | 2040 | 3.7816
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | A,G |  | ctrl | 2050 | 3.8529
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | A,G |  | lower | 2050 | 3.853
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | A,G |  | upper | 2050 | 3.853
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2020
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | lower | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | upper | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2030
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2040
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | lower | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | upper | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (heatpump, installation incl) [2020-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2020 | J | 2, 4 | ctrl | 2020 | 0.26823
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (heatpump, installation incl) [2020-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2020 | J | 2, 4 | ctrl | 2025 | 0.26094
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (heatpump, installation incl) [2020-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2020 | J | 2, 4 | lower | 2025 | 0.2218
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (heatpump, installation incl) [2020-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2020 | J | 2, 4 | upper | 2025 | 0.30008
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (heatpump, installation incl) [2020-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2020 | J | 2, 4 | ctrl | 2030 | 0.25384
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (heatpump, installation incl) [2020-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2020 | J | 2, 4 | ctrl | 2040 | 0.24694
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (heatpump, installation incl) [2020-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2020 | J | 2, 4 | ctrl | 2050 | 0.24023
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (heatpump, installation incl) [2020-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2020 | J | 2, 4 | lower | 2050 | 0.20419
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (heatpump, installation incl) [2020-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2020 | J | 2, 4 | upper | 2050 | 0.27626
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (surface installation excl. heatpump) [2020-MEUR/MW_h] | Nominal investment | surface installation excl. heatpump | MEUR/MW_h | 2020 | J |  | ctrl | 2020 | 0.40235
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (surface installation excl. heatpump) [2020-MEUR/MW_h] | Nominal investment | surface installation excl. heatpump | MEUR/MW_h | 2020 | J |  | ctrl | 2025 | 0.39141
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (surface installation excl. heatpump) [2020-MEUR/MW_h] | Nominal investment | surface installation excl. heatpump | MEUR/MW_h | 2020 | J |  | lower | 2025 | 0.3327
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (surface installation excl. heatpump) [2020-MEUR/MW_h] | Nominal investment | surface installation excl. heatpump | MEUR/MW_h | 2020 | J |  | upper | 2025 | 0.45012
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (surface installation excl. heatpump) [2020-MEUR/MW_h] | Nominal investment | surface installation excl. heatpump | MEUR/MW_h | 2020 | J |  | ctrl | 2030 | 0.38077
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (surface installation excl. heatpump) [2020-MEUR/MW_h] | Nominal investment | surface installation excl. heatpump | MEUR/MW_h | 2020 | J |  | ctrl | 2040 | 0.37041
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (surface installation excl. heatpump) [2020-MEUR/MW_h] | Nominal investment | surface installation excl. heatpump | MEUR/MW_h | 2020 | J |  | ctrl | 2050 | 0.36034
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (surface installation excl. heatpump) [2020-MEUR/MW_h] | Nominal investment | surface installation excl. heatpump | MEUR/MW_h | 2020 | J |  | lower | 2050 | 0.30629
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (surface installation excl. heatpump) [2020-MEUR/MW_h] | Nominal investment | surface installation excl. heatpump | MEUR/MW_h | 2020 | J |  | upper | 2050 | 0.41439
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (wells and down hole eq.) [2020-MEUR/MW_h] | Nominal investment | wells and down hole eq. | MEUR/MW_h | 2020 |  | 2, 4 | ctrl | 2020 | 0.67059
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (wells and down hole eq.) [2020-MEUR/MW_h] | Nominal investment | wells and down hole eq. | MEUR/MW_h | 2020 |  | 2, 4 | ctrl | 2025 | 0.65235
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (wells and down hole eq.) [2020-MEUR/MW_h] | Nominal investment | wells and down hole eq. | MEUR/MW_h | 2020 |  | 2, 4 | lower | 2025 | 0.5545
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (wells and down hole eq.) [2020-MEUR/MW_h] | Nominal investment | wells and down hole eq. | MEUR/MW_h | 2020 |  | 2, 4 | upper | 2025 | 0.7502
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (wells and down hole eq.) [2020-MEUR/MW_h] | Nominal investment | wells and down hole eq. | MEUR/MW_h | 2020 |  | 2, 4 | ctrl | 2030 | 0.63461
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (wells and down hole eq.) [2020-MEUR/MW_h] | Nominal investment | wells and down hole eq. | MEUR/MW_h | 2020 |  | 2, 4 | ctrl | 2040 | 0.61735
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (wells and down hole eq.) [2020-MEUR/MW_h] | Nominal investment | wells and down hole eq. | MEUR/MW_h | 2020 |  | 2, 4 | ctrl | 2050 | 0.60056
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (wells and down hole eq.) [2020-MEUR/MW_h] | Nominal investment | wells and down hole eq. | MEUR/MW_h | 2020 |  | 2, 4 | lower | 2050 | 0.51048
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (wells and down hole eq.) [2020-MEUR/MW_h] | Nominal investment | wells and down hole eq. | MEUR/MW_h | 2020 |  | 2, 4 | upper | 2050 | 0.69065
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | E,J | 2, 4 | ctrl | 2020 | 18791.9463
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | E,J | 2, 4 | ctrl | 2025 | 18255.0336
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | E,J | 2, 4 | lower | 2025 | 15516.7785
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | E,J | 2, 4 | upper | 2025 | 20993.2886
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | E,J | 2, 4 | ctrl | 2030 | 17718.1208
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | E,J | 2, 4 | ctrl | 2040 | 17104.5062
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | E,J | 2, 4 | ctrl | 2050 | 16567.5935
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | E,J | 2, 4 | lower | 2050 | 14082.4545
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2020 | E,J | 2, 4 | upper | 2050 | 19052.7325
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2020 | 1.3412
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2025 | 1.3047
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | lower | 2025 | 1.109
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | upper | 2025 | 1.5004
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2030 | 1.2692
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2040 | 1.2347
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2050 | 1.2011
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | lower | 2050 | 1.021
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | upper | 2050 | 1.3813
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 |  |  | ctrl | 2020
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 |  |  | ctrl | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 |  |  | lower | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 |  |  | upper | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 |  |  | ctrl | 2030
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 |  |  | ctrl | 2040
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 |  |  | ctrl | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 |  |  | lower | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Startup cost [2020-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2020 |  |  | upper | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | F,J | 2, 4 | ctrl | 2020 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | F,J | 2, 4 | ctrl | 2025 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | F,J | 2, 4 | lower | 2025 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | F,J | 2, 4 | upper | 2025 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | F,J | 2, 4 | ctrl | 2030 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | F,J | 2, 4 | ctrl | 2040 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | F,J | 2, 4 | ctrl | 2050 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | F,J | 2, 4 | lower | 2050 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2020 | F,J | 2, 4 | upper | 2050 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M |  | ctrl | 2020 | 0
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M |  | ctrl | 2025 | 0
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M |  | lower | 2025 | 0
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M |  | upper | 2025 | 0
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M |  | ctrl | 2030 | 0
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M |  | ctrl | 2040 | 0
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M |  | ctrl | 2050 | 0
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M |  | lower | 2050 | 0
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (electricity cost) [2020-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2020 | M |  | upper | 2050 | 0
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | F | 2, 4 | ctrl | 2020 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | F | 2, 4 | ctrl | 2025 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | F | 2, 4 | lower | 2025 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | F | 2, 4 | upper | 2025 | 3
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | F | 2, 4 | ctrl | 2030 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | F | 2, 4 | ctrl | 2040 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | F | 2, 4 | ctrl | 2050 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | F | 2, 4 | lower | 2050 | 2.02
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Variable O&M (other O&M) [2020-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2020 | F | 2, 4 | upper | 2050 | 3
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2020 | 10
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2025 | 10
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2025 | 10
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2025 | 10
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2030 | 10
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2040 | 10
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2050 | 10
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2050 | 10
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2050 | 10
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | 2; 5 | ctrl | 2020 | 0.2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | 2; 5 | ctrl | 2025 | 0.2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | 2; 5 | lower | 2025 | 0.2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | 2; 5 | upper | 2025 | 0.2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | 2; 5 | ctrl | 2030 | 0.2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | 2; 5 | ctrl | 2040 | 0.2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | 2; 5 | ctrl | 2050 | 0.2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | 2; 5 | lower | 2050 | 0.2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | 2; 5 | upper | 2050 | 0.2
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2040
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2025
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2040
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2025 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2025 | 3
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2025 | 5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2040 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050 | 4
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050 | 3
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050 | 5
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1, 2 | ctrl | 2020 | 2000
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1, 2 | ctrl | 2025 | 2000
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1, 2 | lower | 2025 | 2000
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1, 2 | upper | 2025 | 2000
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1, 2 | ctrl | 2030 | 2000
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1, 2 | ctrl | 2040 | 2000
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1, 2 | ctrl | 2050 | 2000
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1, 2 | lower | 2050 | 2000
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1, 2 | upper | 2050 | 2000
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | I,A,L,N | 2 | ctrl | 2020 | 100
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | I,A,L,N | 2 | ctrl | 2025 | 100
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | I,A,L,N | 2 | lower | 2025 | 85
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | I,A,L,N | 2 | upper | 2025 | 115
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | I,A,L,N | 2 | ctrl | 2030 | 100
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | I,A,L,N | 2 | ctrl | 2040 | 100
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | I,A,L,N | 2 | ctrl | 2050 | 100
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | I,A,L,N | 2 | lower | 2050 | 85
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | I,A,L,N | 2 | upper | 2050 | 115
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 2 | ctrl | 2020 | 21
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 2 | ctrl | 2025 | 20.769
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 2 | lower | 2025 | 17.6537
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 2 | upper | 2025 | 23.8844
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 2 | ctrl | 2030 | 20.3844
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 2 | ctrl | 2040 | 19.6692
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 2 | ctrl | 2050 | 19.3241
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 2 | lower | 2050 | 16.4255
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 2 | upper | 2050 | 22.2227
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | A, N |  | ctrl | 2020 | 3.77
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | A, N |  | ctrl | 2025 | 3.8119
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | A, N |  | lower | 2025 | 3.81
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | A, N |  | upper | 2025 | 3.81
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | A, N |  | ctrl | 2030 | 3.8838
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | A, N |  | ctrl | 2040 | 4.0251
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | A, N |  | ctrl | 2050 | 4.097
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | A, N |  | lower | 2050 | 4.1
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | A, N |  | upper | 2050 | 4.1
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Nominal Abandonment Cost (ABEX) [2020-MEUR/MW_h] | Nominal Abandonment Cost | ABEX | MEUR/MW_h | 2020 | O | 2, 7 | ctrl | 2020 | 0.10059
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Nominal Abandonment Cost (ABEX) [2020-MEUR/MW_h] | Nominal Abandonment Cost | ABEX | MEUR/MW_h | 2020 | O | 2, 7 | ctrl | 2025 | 0.097852
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Nominal Abandonment Cost (ABEX) [2020-MEUR/MW_h] | Nominal Abandonment Cost | ABEX | MEUR/MW_h | 2020 | O | 2, 7 | lower | 2025 | 0.083175
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Nominal Abandonment Cost (ABEX) [2020-MEUR/MW_h] | Nominal Abandonment Cost | ABEX | MEUR/MW_h | 2020 | O | 2, 7 | upper | 2025 | 0.11253
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Nominal Abandonment Cost (ABEX) [2020-MEUR/MW_h] | Nominal Abandonment Cost | ABEX | MEUR/MW_h | 2020 | O | 2, 7 | ctrl | 2030 | 0.095191
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Nominal Abandonment Cost (ABEX) [2020-MEUR/MW_h] | Nominal Abandonment Cost | ABEX | MEUR/MW_h | 2020 | O | 2, 7 | ctrl | 2040 | 0.092603
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Nominal Abandonment Cost (ABEX) [2020-MEUR/MW_h] | Nominal Abandonment Cost | ABEX | MEUR/MW_h | 2020 | O | 2, 7 | ctrl | 2050 | 0.090084
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Nominal Abandonment Cost (ABEX) [2020-MEUR/MW_h] | Nominal Abandonment Cost | ABEX | MEUR/MW_h | 2020 | O | 2, 7 | lower | 2050 | 0.076572
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Nominal Abandonment Cost (ABEX) [2020-MEUR/MW_h] | Nominal Abandonment Cost | ABEX | MEUR/MW_h | 2020 | O | 2, 7 | upper | 2050 | 0.1036
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L, N | 2 | ctrl | 2020 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L, N | 2 | ctrl | 2025 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L, N | 2 | lower | 2025 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L, N | 2 | upper | 2025 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L, N | 2 | ctrl | 2030 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L, N | 2 | ctrl | 2040 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L, N | 2 | ctrl | 2050 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L, N | 2 | lower | 2050 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L, N | 2 | upper | 2050 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of production wells | Number of production wells |  |  |  | L | 2 | ctrl | 2020 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of production wells | Number of production wells |  |  |  | L | 2 | ctrl | 2025 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of production wells | Number of production wells |  |  |  | L | 2 | lower | 2025 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of production wells | Number of production wells |  |  |  | L | 2 | upper | 2025 | 12
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of production wells | Number of production wells |  |  |  | L | 2 | ctrl | 2030 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of production wells | Number of production wells |  |  |  | L | 2 | ctrl | 2040 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of production wells | Number of production wells |  |  |  | L | 2 | ctrl | 2050 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of production wells | Number of production wells |  |  |  | L | 2 | lower | 2050 | 6
45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Technology-specific data | Number of production wells | Number of production wells |  |  |  | L | 2 | upper | 2050 | 12
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | ctrl | 2020 | 2.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | ctrl | 2025 | 2.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | lower | 2025 | 2
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | upper | 2025 | 3
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | ctrl | 2030 | 2.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | ctrl | 2040 | 2.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | ctrl | 2050 | 2
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | lower | 2050 | 1.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | upper | 2050 | 2.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.019087
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2025 | 0.017588
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2025 | 0.017588
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2025 | 0.017588
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.017496
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2040 | 0.017316
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.017139
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.017139
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.017139
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | ctrl | 2020 | 8.4
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | ctrl | 2025 | 15
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | lower | 2025 | 12.75
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | upper | 2025 | 17.25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | ctrl | 2030 | 20
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | ctrl | 2040 | 25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | ctrl | 2050 | 30
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | lower | 2050 | 22.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | upper | 2050 | 37.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2020 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2025 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | lower | 2025 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | upper | 2025 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2030 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2040 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2050 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | lower | 2050 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | upper | 2050 | 0.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | ctrl | 2020 | 165.355
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | ctrl | 2025 | 177.3605
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | lower | 2025 | 150.7565
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | upper | 2025 | 203.9646
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | ctrl | 2030 | 171.9641
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | ctrl | 2040 | 169.841
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | ctrl | 2050 | 171.2564
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | lower | 2050 | 128.4423
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | upper | 2050 | 214.0705
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | ctrl | 2020 | 27
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | ctrl | 2025 | 30
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | lower | 2025 | 25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | upper | 2025 | 35
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | ctrl | 2030 | 30
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | ctrl | 2040 | 30
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | ctrl | 2050 | 30
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | lower | 2050 | 25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | upper | 2050 | 35
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2020 | 50000
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2025 | 42000
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | lower | 2025 | 35700
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | upper | 2025 | 48300
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2030 | 39000
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2040 | 34000
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2050 | 33000
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | lower | 2050 | 24750
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | upper | 2050 | 49500
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2020 | 2.1159
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2025 | 1.8837
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | lower | 2025 | 1.8837
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | upper | 2025 | 1.8837
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2030 | 1.7954
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2040 | 1.6764
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2050 | 1.6427
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | lower | 2050 | 1.6427
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | upper | 2050 | 1.6427
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.53911
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.40406
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.40406
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 0.40406
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.36506
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.33266
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.31708
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.31708
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 0.31708
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | ctrl | 2020 | 5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | ctrl | 2025 | 4.1721
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | lower | 2025 | 3.5463
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | upper | 2025 | 4.7979
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | ctrl | 2030 | 3.8947
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | ctrl | 2040 | 3.4208
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | ctrl | 2050 | 3.2519
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | lower | 2050 | 2.4389
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | upper | 2050 | 4.8779
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2020
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2030
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2040
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2040
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2040
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2040
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2025
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2040
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | ctrl | 2020 | 4400
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | ctrl | 2025 | 4775
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | lower | 2025 | 4300
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | upper | 2025 | 5250
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | ctrl | 2030 | 4800
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | ctrl | 2040 | 4850
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | ctrl | 2050 | 4900
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | lower | 2050 | 4050
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | upper | 2050 | 5500
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | ctrl | 2020 | 103.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | ctrl | 2025 | 138
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | lower | 2025 | 124.2
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | upper | 2025 | 151.8
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | ctrl | 2030 | 155
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | ctrl | 2040 | 170
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | ctrl | 2050 | 185
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | lower | 2050 | 157.25
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | upper | 2050 | 212.75
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2020 | 0.38081
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2025 | 0.31068
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | lower | 2025 | 0.26408
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | upper | 2025 | 0.35728
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2030 | 0.28378
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2040 | 0.2451
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2050 | 0.22896
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | lower | 2050 | 0.17172
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | upper | 2050 | 0.34344
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.02614
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.019706
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.01675
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 0.022662
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.016604
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.014302
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.012951
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.0097129
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 0.019426
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2020 | 0.20689
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2025 | 0.21461
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | lower | 2025 | 0.18242
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | upper | 2025 | 0.24681
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2030 | 0.21768
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2040 | 0.22033
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2050 | 0.2127
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | lower | 2050 | 0.15953
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | upper | 2050 | 0.31905
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2020 | 0.24667
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2025 | 0.23966
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | lower | 2025 | 0.20371
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | upper | 2025 | 0.2756
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2030 | 0.24096
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2040 | 0.25053
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2050 | 0.2643
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | lower | 2050 | 0.19822
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | upper | 2050 | 0.39645
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.71632
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.69499
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.59074
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 0.79923
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.67129
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.61348
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.60676
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.45507
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 0.91014
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | ctrl | 2020 | 167
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | ctrl | 2025 | 236
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | lower | 2025 | 212.4
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | upper | 2025 | 259.6
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | ctrl | 2030 | 270
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | ctrl | 2040 | 300
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | ctrl | 2050 | 330
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | lower | 2050 | 280.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | upper | 2050 | 379.5
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | ctrl | 2020 | 6.0476
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | ctrl | 2025 | 5.6382
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | lower | 2025 | 6.6332
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | upper | 2025 | 4.9028
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | ctrl | 2030 | 5.8152
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | ctrl | 2040 | 5.8879
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | ctrl | 2050 | 5.8392
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | lower | 2050 | 7.7856
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | upper | 2050 | 4.6714
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | ctrl | 2020 | 383.4921
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | ctrl | 2025 | 342.9078
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | lower | 2025 | 359.8415
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | upper | 2025 | 325.9041
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | ctrl | 2030 | 349.3113
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | ctrl | 2040 | 353.6777
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | ctrl | 2050 | 350.7547
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | lower | 2050 | 364.1052
21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | upper | 2050 | 331.5262
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | ctrl | 2020 | 2.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | ctrl | 2025 | 2.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | lower | 2025 | 2
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | upper | 2025 | 3
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | ctrl | 2030 | 2.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | ctrl | 2040 | 2.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | ctrl | 2050 | 2
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | lower | 2050 | 1.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | D |  | upper | 2050 | 2.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.020483
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2025 | 0.019417
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2025 | 0.019417
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2025 | 0.019417
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.018872
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2040 | 0.018872
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.018872
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.018872
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.018872
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | ctrl | 2020 | 8.4
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | ctrl | 2025 | 10
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | lower | 2025 | 8.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | upper | 2025 | 11.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | ctrl | 2030 | 15
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | ctrl | 2040 | 15
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | ctrl | 2050 | 15
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | lower | 2050 | 11.25
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | 1, 2 | upper | 2050 | 18.75
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2020 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2025 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | lower | 2025 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | upper | 2025 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2030 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2040 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2050 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | lower | 2050 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | upper | 2050 | 0.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | ctrl | 2020 | 32.0212
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | ctrl | 2025 | 35.1844
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | lower | 2025 | 29.9067
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | upper | 2025 | 40.4621
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | ctrl | 2030 | 35.811
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | ctrl | 2040 | 35.811
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | ctrl | 2050 | 35.811
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | lower | 2050 | 26.8582
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | E | 3 | upper | 2050 | 44.7637
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | ctrl | 2020 | 27
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | ctrl | 2025 | 30
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | lower | 2025 | 25
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | upper | 2025 | 35
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | ctrl | 2030 | 30
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | ctrl | 2040 | 30
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | ctrl | 2050 | 30
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | lower | 2050 | 25
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C |  | upper | 2050 | 35
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2020 | 50000
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2025 | 42000
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | lower | 2025 | 35700
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | upper | 2025 | 48300
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2030 | 39000
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2040 | 34000
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | ctrl | 2050 | 33000
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | lower | 2050 | 24750
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Fixed O&M (*total) [2020-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2020 | H | 3 | upper | 2050 | 49500
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2020 | 1.6999
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2025 | 1.488
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | lower | 2025 | 1.488
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | upper | 2025 | 1.488
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2030 | 1.3844
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2040 | 1.2384
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2050 | 1.1859
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | lower | 2050 | 1.1859
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | upper | 2050 | 1.1859
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.38968
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.3138
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.3138
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 0.3138
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.25365
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.22841
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.21927
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.21927
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (installation) [2020-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 0.21927
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | ctrl | 2020 | 5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | ctrl | 2025 | 4.1721
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | lower | 2025 | 3.5463
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | upper | 2025 | 16.6885
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | ctrl | 2030 | 3.8947
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | ctrl | 2040 | 3.4208
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | ctrl | 2050 | 3.2519
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | lower | 2050 | 2.4389
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Variable O&M (*total) [2020-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2020 | H | 3 | upper | 2050 | 13.0076
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2020
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2030
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2040
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2040
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2040
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2040
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2025
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2040
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | ctrl | 2020 | 4100
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | ctrl | 2025 | 4325
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | lower | 2025 | 3675
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | upper | 2025 | 4975
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | ctrl | 2030 | 4450
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | ctrl | 2040 | 4450
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | ctrl | 2050 | 4450
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | lower | 2050 | 3250
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | J | 3 | upper | 2050 | 6500
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | ctrl | 2020 | 103.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | ctrl | 2025 | 115.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | lower | 2025 | 98.175
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | upper | 2025 | 132.825
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | ctrl | 2030 | 138
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | ctrl | 2040 | 138
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | ctrl | 2050 | 138
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | lower | 2050 | 103.5
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | 1 | upper | 2050 | 207
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2020 | 0.39435
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2025 | 0.32741
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | lower | 2025 | 0.2783
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | upper | 2025 | 1.3096
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2030 | 0.29454
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2040 | 0.25871
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | ctrl | 2050 | 0.24593
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | lower | 2050 | 0.18445
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (project development etc.) [2020-MEUR/MW_e] | Nominal investment | project development etc. | MEUR/MW_e | 2020 |  | 3, 6 | upper | 2050 | 0.98374
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.012591
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.011578
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.009841
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 0.04631
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.0093792
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.0090889
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.0089781
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.0067336
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (array cables) [2020-MEUR/MW_e] | Nominal investment | array cables | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 0.035912
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2020 | 0.13493
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2025 | 0.12851
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | lower | 2025 | 0.10924
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | upper | 2025 | 0.51406
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2030 | 0.12325
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2040 | 0.11009
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | ctrl | 2050 | 0.10535
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | lower | 2050 | 0.079011
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (foundation) [2020-MEUR/MW_e] | Nominal investment | foundation | MEUR/MW_e | 2020 |  | 3, 4 | upper | 2050 | 0.42139
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2020 | 0.052
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2025 | 0.049769
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | lower | 2025 | 0.042303
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | upper | 2025 | 0.19907
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2030 | 0.048946
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2040 | 0.047431
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | ctrl | 2050 | 0.046853
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | lower | 2050 | 0.03514
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2020-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2020 |  | 3, 5 | upper | 2050 | 0.18741
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | ctrl | 2020 | 0.71632
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | ctrl | 2025 | 0.65694
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | lower | 2025 | 0.5584
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | upper | 2025 | 2.6278
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | ctrl | 2030 | 0.65458
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | ctrl | 2040 | 0.58469
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | ctrl | 2050 | 0.55948
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | lower | 2050 | 0.41961
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (turbines) [2020-MEUR/MW_e] | Nominal investment | turbines | MEUR/MW_e | 2020 |  | 3 | upper | 2050 | 2.2379
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | ctrl | 2020 | 167
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | ctrl | 2025 | 191
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | lower | 2025 | 162.35
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | upper | 2025 | 219.65
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | ctrl | 2030 | 236
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | ctrl | 2040 | 236
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | ctrl | 2050 | 236
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | lower | 2050 | 177
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  |  | 1 | upper | 2050 | 354
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | ctrl | 2020 | 31.2293
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | ctrl | 2025 | 28.4217
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | lower | 2025 | 33.4373
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | upper | 2025 | 24.7145
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | ctrl | 2030 | 27.9244
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | ctrl | 2040 | 27.9244
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | ctrl | 2050 | 27.9244
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | lower | 2050 | 37.2325
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific area coverage [MW_e/km2] | Specific area coverage |  | MW_e/km2 |  | E | 3 | upper | 2050 | 22.3395
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | ctrl | 2020 | 383.4921
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | ctrl | 2025 | 349.0144
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | lower | 2025 | 410.6052
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | upper | 2025 | 303.4908
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | ctrl | 2030 | 342.9078
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | ctrl | 2040 | 342.9078
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | ctrl | 2050 | 342.9078
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | lower | 2050 | 457.2104
21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  | I | 1 | upper | 2050 | 190.5043

## 01 Coal CHP
Technology |  | Coal power plant, supercritical - extraction - coal - medium
year |  | 2015 | 2020 | 2030 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 500 | 500 | 500 | 500
| Electrical efficiency (net, name plate) [] | 46% | 48.5% | 52% | 53.5% | C | [8, 7, 9, 11]
| Cb coefficient (50°C/100°C) | 0.75 | 0.84 | 1.01 |  | A
| Cv coefficient (50°C/100°C) | 0.15 | 0.15 | 0.15 |  |  | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 |  | 6
| Construction time [years] | 4.5 | 4.5 | 4.5 |  |  | [2, 3, 3]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | D | 14
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | D | 14
| Minimum load (of full load) [] | 18% | 15% | 15% | 10% |  | [10, 14]
Environment
| SO2 (degree of desulphuring) [] | 97% | 97% | 97% | 97% | B | 5
| NOX [g/GJ_i] | 38 | 35 | 35 | 35 | B | [12, 5, 5, 5]
| CH4 [g/GJ_i] | 1.5 | 1.5 | 1.5 | 1.5 |  | [13, 5, 5, 5]
| N2O [g/GJ_i] | 0.8 | 0.8 | 0.8 | 0.8 |  | [13, 5, 5, 5]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 1.93 | 1.9 | 1.86 | 1.78 | J | [17, 18, 19, 20, 21, 22]
| Variable O&M (*total) [2015-EUR/MWh_e] | 2.95 | 2.9 | 2.84 | 2.72 | J | [17, 18, 19, 20, 21, 22]
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 31500 | 31000 | 30355.12 | 29105.32 | J | [17, 18, 19, 20, 21, 22]
Technology-specific data
| Availability [] | 95% | 95% | 95% |  | E | 7
Notes:
A. The Cb values have been calculated from the electricity efficiencies in condensation mode, the Cv values and a total efficiency (electricity plus heat) in full back-pressure mode of 90%. Cf. Annex 1.
B. The data for SO2 and NOx emissions assume flue gas desulphurisation (wet gypsum) and DeNOx equipment of the "high dust" SCR type.
C. Supercritical in 2010 and ultra-supercritical from 2020.
D. Please refer to section 'Regulation ability' in the above qualitative description.
E. Outage rates are generally about 5% for plants that are 10-20 years old. Unless the plant is refurbished, the rate increases to 20% for plants that are 40 years old (ref. 7)
F. It is assumed that the cost is falling by 0.2 % p.a. Defaltor 2011-2015: 1.059
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Elsam, November 2003
2. Elsam's and Elkraft's update of the Danish Energy Agency's 'Teknologidata for el- og varmeproduktionsanlæg', December 1997
3. Eltra, September 2003
5. Danish Energy Agency, 2009.
6. "Projected costs of generating electricity", International Energy Agency (IEA), 2005.
7. "Energy technology perspectives 2008", International Energy Agency, 2008.
8. Danish Energy Agency, 2008. Measured data (1994-2006) from newest power plants in Denmark.
9. Own estimate by Danish Energy Agency and Energinet.dk, 2011.
10. Energinet.dk, 2009
11. www.ad700.dk
12. "En opdateret analyse af Danmarks muligheder for at reducere emissionerne af NOx" (Updated analysis of Denmark's options to reduce NOx emissions; in Danish), Danish Environmental Protection Agency, 2009.
13. National Environmental Research Institute, Denmark, 2009 (data from 2007).
14. DONG Energy, 2009.
15. "UK Electricity Generation Costs Update", Mott MacDonald, June 2010.
16. "The Costs of CO2 Capture, Transport and Storage", Zero Emissions Platform (ZEP), July 2011
17. The IEA World Energy Outlook 2014 coal fired Ultra-supercritical power plants in Europe. Values used are the projection for 2020.
18. The IEA Projected Cost of Generating Electricity 2015 for coal fired power plants. Here both the 'world median' is used, and data from recently commissioned plants in the Netherlands. The three units in the Netherlands are chosen because of the proximity to Denmark, because the socio-economic parameters (labour cost etc) are assumed to be similar and because the units are new (all from 2015).
19. EIA Updated Capital Cost Estimates for Utility Scale Electricity Generating Plants 2013 for pulverizes coal fired advanced single units.[1]
20. Aggregated data from different projects on existing units that Ea Energy Analyses have been working on since 2010. Data is used for estimating O&M costs.
21. IEA( 2016),Energy Technology Perspectives
22. E.S. Rubin et al. / Energy Policy 86 (2015) page 198-218, A review of learning rates for electricity supply technologies

## 02 LTE existing plant
Technology |  | Life time extension of coal extraction plant - refurbish - coal - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 300 | 300 | 300 |  | 200 | 400 | 200 | 400
| Electrical efficiency (net, annual average, additional to existing plant) [] | 0% | 0% | 0% |  | -1% | 1% |  |  | [E, F] | 7
| Electrical efficiency (net, name plate, additional to existing plant) [] | 0% | 0% | 0% |  | -1% | 1% |  |  | [E, F] | 7
| Cb coefficient (50°C/100°C, additional to existing plant) | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F] | 7
| Cv coefficient (50°C/100°C, additional to existing plant) | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F] | 7
| Forced outage (additional to existing plant) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | [A, F] | 7
| Planned outage (additional to existing plant) [weeks per year] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F] | 7
| Technical lifetime [years] | ctrl: 15; ctrl: 15; ctrl: 15; ref: [4, 5, 6, 7]
| Construction time [years] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ref: 7
| Space requirement (additional to existing plant) [1000 m2/MW_e] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F]
Regulation ability
| Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | [A, F] | 7
| Secondary regulation (of full load, additional to existing plant, per minute) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | [A, F] | 7
| Minimum load (of full load, additional to existing plant) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | [A, F] | 7
| Warm start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F] | 7
| Cold start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F] | 7
Environment
| SO2 (degree of desulphuring, additional to existing plant) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | [A, F, G] | 8
| NOX (additional to existing plant) [g/GJ_i] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F, G] | 8
| CH4 (additional to existing plant) [g/GJ_i] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F, G] | 8
| N2O (additional to existing plant) [g/GJ_i] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, F, G] | 8
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 0.24 | 0.24 | 0.24 |  | 0.15 | 0.34 |  |  | [C, F] | [4, 5, 6, 7]
Nominal investment (equipment) [2015-MEUR/MW_e]
Nominal investment (installation) [2015-MEUR/MW_e]
| Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, D, F] | 7
| Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | 0 | 0 | 0 |  | 0 | 8000 |  |  | [A, B, F] | 7
Notes:
A. Values will generally be similar to those of the plant prior to Life Time Extention (LTE).
B. Values will depend on those of the plant prior to LTE, however the average fixed O&M cost may increase slightly for the extension period compared with the original life time to accomodate the necessary reinvestments during the extended life time.
C. Investment costs will vary largely, depending on the necessary scope of work. The indicated range represents typical cases where 20-25 years Danish coal power CHP plants have been life time extended to obtain additional 15 years life time (based mainly on budgetted values).
D. Variable O&M costs will in general be similar or a bit smaller to those of the plant prior to LTE. The reason for the small improvement is when you compare it to just before the LTE. When compared to the average over the lifetime the O&M costs will be similar.
E. Values will generally be similar to those of the plant prior to LTE. Average efficiencies over the lifetime will be similar to the plant prior to LTE, but the efficiencies just after the LTE will be better than that of the plant just before the LTE.
F. Values for year 2050 are not considered relevant since new coal fired power plants are not expected to be built
G. It is assumed that plants emissions prior to the LTE is within the legal limits.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
4. Projected Costs of Generating electricity edition 2015, IEA, NEA and OECD 2015
5. Baggrundsnotat omhandlende metode for Energinet.dk's forventninger til kraftværksudviklingen i Danmark, Energinet.dk, 27. august 2014 (Background note concerning method for Energinet.dk's expectations for power plant development in Denmark , Energinet.dk , August 27, 2014)
6. Studstrupværket kører videre på kul frem til 2015, Ingeniøren, 10. maj 2012,( Studstrupværket continues to run on coal until 2015, Engineer , May 10, 2012, )
7. Ea Energy Analysis, based on experience from various commercial projects.
8. It is assumed by Ea Energy Analyses that plants emissions prior to the LTE is within the legal limits.

## 03a Coal to wood pellets exi bo
Technology |  | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 300; ctrl: 300; ctrl: 300; lower: 200; upper: 400
| Electrical efficiency (net, annual average, additional to existing plant) [] | -1% | -1% | -1% |  | 0% | -2% |  |  | [A, B, C, I] | 10
| Electrical efficiency (net, name plate, additional to existing plant) [] | -1% | -1% | -1% |  | 0% | -2% |  |  | [A, B, C, I] | 10
| Cb coefficient (50°C/100°C, additional to existing plant) | -0.02 | -0.02 | -0.02 |  | 0 | -0.05 |  |  | [A, B, C, I] | 10
| Cv coefficient (50°C/100°C, additional to existing plant) | 0 | 0 | 0 |  | -0.01 | 0.01 |  |  | [A, C] | 10
| Forced outage (additional to existing plant) [] | 0% | 0% | 0% |  | -1% | 1% |  |  | A | 10
| Planned outage (additional to existing plant) [weeks per year] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
| Technical lifetime [years] | ctrl: 15; ctrl: 15; ctrl: 15; note: C; ref: 10
| Construction time [years] | 2 | 2 | 2 |  | 1.5 | 2.5 |  |  | C | 10
| Space requirement (additional to existing plant) [1000 m2/MW_e] | 0 | 0 | 0 |  | 0 | 0 |  |  | [A, D]
Regulation ability
| Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Secondary regulation (of full load, additional to existing plant, per minute) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Minimum load (of full load, additional to existing plant) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Warm start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
| Cold start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
Environment
SO2 (degree of desulphuring) [] | bar: note
| NOX [g/GJ_i] | 20 | 21 | 18 |  | 19 | 53 |  |  | G
| CH4 [g/GJ_i] | 0 | 0 | 0 |  | 3.1 | 3.1 |  |  | G
| N2O [g/GJ_i] | 1 | 1 | 1 |  | 0.8 | 0.8 |  |  | G
| Particles [g/GJ_i] | ctrl: 0.3; ctrl: 0.3; ctrl: 0.3
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 0.5 | 0.5 | 0.5 |  | 0.35 | 0.8 |  |  | [C, E, K] | [10, 11, 12]
Nominal investment (equipment) [2015-MEUR/MW_e]
Nominal investment (installation) [2015-MEUR/MW_e]
| Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | 0.9 | 0.9 | 0.9 |  | 0.4 | 1.4 |  |  | [A, F, K] | 10
| Fixed O&M [EUR/MWe/year] | 3350 | 3350 | 3350 |  | 1350 | 5350 |  |  | [A, F, K] | 10
Technology-specific data
| Variable O&M (*total, additional to existing plantl) [2015-EUR/MWh_i] | 0.36 | 0.36 | 0.36 |  | 0.16 | 0.56 |  |  | [A, F, K] | 10
| Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_i/y] | 1350 | 1350 | 1350 |  | 550 | 2150 |  |  | [A, F, K] | 10
Notes:
A. Value depend on the original plant. Value indicate the estimated change from the original value (unit is the same as the paramter).
B. Typically the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion. The thermal efficiency is typically unchanged, thus the Cb value decreases, meaning more heat is produced compared to electricity.
C. Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
D. Some additional under roof space (or silos) will be required for storage of pellets compared to coal (estimated 50%-100% extra m3 storage). But not more floor space (m2).
E. The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
F. The variable O&M costs will be similar to those of the original plant, however fixed O&M costs are likely to increase by 10-20%
G. Assumed the same emission values from the datasheet of new biomass plants (wood chips). See references and notes in the datasheet '09 Biomass CHP, Steam Turbine - Large steam turbine, Woodchips'.
I. It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.556. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient of 0.77. The estimates are made based on Danish CHP plants that are commissioned in 1990, 1995 and 2005.
J. It is assumed that that Flue Gas Desulphurization plant is bypassed (stopped) due to low Sulphur content in wood pellet fuel
K. O&M cost and CAPEX has been estimated by Ramboll in April 2019 based on input from DE/Ørsted and data from UK Department for Business, Energy & Industry strategy (BEIS) in their Electricity Generation Cost report from 2016.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
10. Ea Energy Analysis, based on experience from various commercial projects.
11. Government response to the consultation on proposals for the levels of banded support under the Renewables Obligation for the period 2013-17 and the Renewables Obligation Order 2012, UK Department of Energy and Climate Change, July 2012.
12. A strategy for converting coal fueled power plants to biomass, Future Metrics, September 2014

## 03b Coal to wood chips n. boile
Technology |  | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 300; ctrl: 300; ctrl: 300; lower: 200; upper: 400
| Electrical efficiency (net, annual average, additional to existing plant) [] | -1% | -1% | -1% |  | 0% | -2% |  |  | [A, B, J] | 10
| Electrical efficiency (net, name plate, additional to existing plant) [] | -1% | -1% | -1% |  | 0% | -2% |  |  | [A, B, J] | 10
| Cb coefficient (50°C/100°C, additional to existing plant) | -0.07 | -0.07 | -0.07 |  | -0.02 | -0.1 |  |  | [A, B, J] | 10
| Cv coefficient (50°C/100°C, additional to existing plant) | 0 | 0 | 0 |  | -0.01 | 0.01 |  |  | A | 10
| Forced outage (additional to existing plant) [] | 0% | 0% | 0% |  | -1% | 1% |  |  | A | 10
| Planned outage (additional to existing plant) [weeks per year] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
| Technical lifetime [years] | ctrl: 15; ctrl: 15; ctrl: 15; note: C; ref: 10
| Construction time [years] | 2.5 | 2.5 | 2.5 |  | 2 | 3 |  |  | C | 10
| Space requirement (additional to existing plant) [1000 m2/MW_e] | 0.03 | 0.03 | 0.03 |  | 0.02 | 0.05 |  |  | [A, D] | 10
Regulation ability
| Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | -2% | 0% | 0% |  | 0% | -5% |  |  | [A, I] | 10
| Secondary regulation (of full load, additional to existing plant, per minute) [] | -2% | 0% | 0% |  | 0% | -5% |  |  | [A, I] | 10
| Minimum load (of full load, additional to existing plant) [] | 0.05% | 0.05% | 0% |  | 0% | 0.1% |  |  | A | 10
| Warm start-up time (additional to existing plant) [hours] | 0.5 | 0.5 | 0 |  | 0 | 2 |  |  | [A, I] | 10
| Cold start-up time (additional to existing plant) [hours] | 1 | 1 | 1 |  | 0 | 2 |  |  | [A, I] | 10
Environment
| SO2 (degree of desulphuring) [] | ctrl: 98%; ctrl: 98%; ctrl: 98%
| NOX [g/GJ_i] | 30 | 24 | 20 |  | 19 | 53 |  |  | G
| CH4 [g/GJ_i] | 3 | 2 | 2 |  | 0 | 0.5 |  |  | G
| N2O [g/GJ_i] | 10 | 8 | 6 |  | 2 | 20 |  |  | G
| Particles [g/GJ_i] | ctrl: 0.3; ctrl: 0.3; ctrl: 0.3
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 1.61 | 1.61 | 1.61 |  | 1.34 | 2.15 |  |  | [C, E] | [10, 12]
Nominal investment (equipment) [2015-MEUR/MW_e]
Nominal investment (installation) [2015-MEUR/MW_e]
| Variable O&M (*total) [2015-EUR/MWh_e] | 2.75 | 2.75 | 2.75 |  | 1.75 | 3.75 |  |  | [F, K] | 10
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 73750 | 73750 | 73750 |  | 61250 | 86250 |  |  | [F, K] | 10
Technology-specific data
| Variable O&M (*total) [2015-EUR/MWh_i] | 1.1 | 1.1 | 1.1 |  | 0.7 | 1.5 |  |  | [F, K] | 10
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 29500 | 29500 | 29500 |  | 24500 | 34500 |  |  | [F, K] | 10
Notes:
A. Value depend on the original plant.
B. Typically the electricity efficiency will be 1-2 % point lower than that of the plant prior to conversion. The thermal efficiency will typically increase to around 105%. thus the Cb value decreases. meaning more heat is produced compared to electricity. This is mainly due to implementation of exhaust gas condenser.
C. Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
D. Some additional space will be required for storage of chips (estimated 50%-100% extra).
E. The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
F. The fixed O&M costs are likely to increase by 10-20%. whereas the variable O&M costs are likely to increase approx. 50%.
G. Emission values from the datasheet of new CFB biomass plants. See references and notes in the datasheet 'Large Biomass Circulating Fluidized Bed Combustion Systems (CFBC) for wood'.
I. The regulation time of the boiler will often increase due to slower burning of chips compared to pulverized fuel. Depending of the other thermal limitations in the cycle (e.g. in the turbines) this will have no change or an increase in the regulation time.
J. It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.56. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient of 0.77. The estimates are made based on Danish CHP plants that are commissioned in 1990, 1995 and 2005.
K. O&M cost are copied from 09 Large Wood Chip CHP corrected with efficiency. Note that all financial data are absolute values and not relative to coal.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
10. Ea Energy Analysis. based on experience from various commercial projects.
12. A strategy for converting coal fueled power plants to biomass. Future Metrics. September 2014

## 03c coal to wood chips exi. boi
Technology |  | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 300; ctrl: 300; ctrl: 300; lower: 200; upper: 400
| Electrical efficiency (net, annual average, additional to existing plant) [] | -3% | -3% | -3% |  | -2% | -4% |  |  | [A, B, I] | 10
| Electrical efficiency (net, name plate, additional to existing plant) [] | -3% | -3% | -3% |  | -2% | -4% |  |  | [A, B, I] | 10
| Cb coefficient (50°C/100°C, additional to existing plant) | -0.07 | -0.07 | -0.07 |  | -0.02 | -0.1 |  |  | [A, B, I] | 10
| Cv coefficient (50°C/100°C, additional to existing plant) | 0 | 0 | 0 |  | -0.01 | 0.01 |  |  | A | 10
| Forced outage (additional to existing plant) [] | 0% | 0% | 0% |  | -1% | 1% |  |  | A | 10
| Planned outage (additional to existing plant) [weeks per year] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
| Technical lifetime [years] | ctrl: 15; ctrl: 15; ctrl: 15; note: C; ref: 10
| Construction time [years] | 2 | 2 | 2 |  | 1.5 | 2.5 |  |  | C | 10
| Space requirement (additional to existing plant) [1000 m2/MW_e] | 0.04 | 0.04 | 0.04 |  | 0.03 | 0.06 |  |  | [A, D] | 10
Regulation ability
| Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Secondary regulation (of full load, additional to existing plant, per minute) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Minimum load (of full load, additional to existing plant) [] | 0% | 0% | 0% |  | 0% | 0% |  |  | A | 10
| Warm start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
| Cold start-up time (additional to existing plant) [hours] | 0 | 0 | 0 |  | 0 | 0 |  |  | A | 10
Environment
| SO2 (degree of desulphuring) [] | ctrl: 98%; ctrl: 98%; ctrl: 98%; note: G
| NOX [g/GJ_i] | 30 | 24 | 20 |  | 19 | 53 |  |  | G
| CH4 [g/GJ_i] | 3 | 2 | 2 |  | 3.1 | 3.1 |  |  | G
| N2O [g/GJ_i] | 10 | 8 | 6 |  | 0.8 | 0.8 |  |  | G
| Particles [g/GJ_i] | ctrl: 0.3; ctrl: 0.3; ctrl: 0.3; note: G
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 1.61 | 1.61 | 1.61 |  | 1.34 | 2.15 |  |  | [C, E] | 10
Nominal investment (equipment) [2015-MEUR/MW_e]
Nominal investment (installation) [2015-MEUR/MW_e]
| Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | 1.5 | 1.5 | 1.5 |  | 1 | 2 |  |  | F | 10
| Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | 14175 | 14175 | 14175 |  | 12600 | 15750 |  |  | F | 10
Notes:
A. Value depend on the original plant.
B. Typically the electricity efficiency will be 3-4 % point lower than that of the plant prior to conversion. The thermal efficiency is increased to approximately 100% because of flue gas condensation in drying process, thus the Cb value decreases, meaning more heat is produced compared to electricity.
C. Values for year 2050 are not considered relevant since it is assumed that all coal fired plants in Denmark have been rebuilt or decommissioned.
D. Some additional space will be required for storage of chips (estimated 50%-100% extra) and for the drying plant.
E. The nominal investment assumes that the original plant is aged and therefore include investment for a general life time extension campaign
F. Both variable and fixed O&M costs are likely to increase by 40-50% from the original plant.
G. Assumed the same emission values from the datasheet of new biomass plants (wood chips). See references and notes in the datasheet '09 Biomass CHP, Steam Turbine - Large steam turbine, Woodchips'.
I. It is assumed that plants that are refurbished in 2015 have an electric efficiency of 41% and a CB coefficient of 0.57. Plants refurbished in 2020 have an electric efficiency of 42% and a CB coefficient of 0.64. Plants refurbished in 2030 have an electric efficiency of 44% and a CB coefficient of 0.77. The estimates are made based on Danish CHP plants that are commissioned in 1990, 1995 and 2005.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
10. Ea Energy Analysis, based on experience from various commercial projects.

## 03d coal to wood chips exi. boi
Technology |  | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 70; lower: 50; upper: 90; note: [A, E]; ref: 13
| Electrical efficiency (net, annual average) [] | ctrl: 0.27%; note: B; ref: 13
| Electrical efficiency (net, name plate) [] | ref: 13
| Cb coefficient (50°C/100°C) | ctrl: 0.35; note: B; ref: 13
| Cv coefficient (50°C/100°C) | ref: 13
| Forced outage [] | ctrl: 3%; note: C; ref: 13
| Planned outage [weeks per year] | ctrl: 1.56; note: C; ref: 13
| Technical lifetime [years] | ctrl: 15
Construction time [years]
Space requirement [1000 m2/MW_e]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | ctrl: 2%; note: C; ref: 13
| Secondary regulation (of full load, per minute) [] | ctrl: 3%; note: C; ref: 13
| Minimum load (of full load) [] | ctrl: 45%; note: C; ref: 13
| Warm start-up time [hours] | ctrl: 2; note: C; ref: 13
| Cold start-up time [hours] | ctrl: 12; note: C; ref: 13
Environment
SO2 (degree of desulphuring) []
| NOX [g/GJ_i] | ctrl: 30; note: C; ref: 13
| CH4 [g/GJ_i] | ctrl: 3; note: C; ref: 13
| N2O [g/GJ_i] | ctrl: 10; note: C; ref: 13
| Particles [g/GJ_i] | ctrl: 0.3; note: C; ref: 13
Financial data
Nominal investment (*total) [2015-MEUR/MW_e]
Nominal investment (equipment) [2015-MEUR/MW_e]
Nominal investment (installation) [2015-MEUR/MW_e]
| Variable O&M (*total) [2015-EUR/MWh_e] | ctrl: 4.07; note: D
| Fixed O&M (*total) [2015-EUR/MW_e/y] | ctrl: 109259.26; note: D
Technology-specific data
| Variable O&M (*total) [2015-EUR/MWh_i] | ctrl: 1.1; note: D
| Fixed O&M (*total) [2015-EUR/MW_i/y] | ctrl: 29500; note: D
Notes:
A. Based on existing converted coal plant 50-90 MW capacity
B. The estimated electrcial efficiency is 27 %. It is assumed that plants are equipped with Flue Gas Condensation having total efficiency of 105 %
C. Values are based on Data sheet for Wood Chips CHP, Large
D. O&M data are based data sheet 09 Wood chips CHP, Large, the specific values based on electricity has been corrected base on efficiency
E. Uncertainty estimate applies for 2015 value
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
13. Ramboll, internal assessment

## 04 Gas turb. simple cycle, L
Technology |  | Gas turbine, simple cycle - back pressure - natural gas - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 40; upper: 125; lower: 40; upper: 125; note: F
| Electrical efficiency (net, name plate) [] | 41% | 42% | 43% | 45% | 38% | 42% | 40% | 44% |  | [6, 12]
| Electrical efficiency (net, annual average) [] | 39% | 40% | 41% | 43% | 36% | 40% | 38% | 42% |  | [6, 11]
| Cb coefficient (50°C/100°C) | 0.95 | 0.96 | 1 | 1 | 0.8 | 1.2 | 0.8 | 1.2 |  | [6, 12]
Cv coefficient (50°C/100°C) | bar: note
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 3% | 2% | 3% |  | 6
| Planned outage [weeks per year] | 3 | 3 | 2.5 | 2.5 | 2 | 3.5 | 1.5 | 3 |  | 6
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | E | [6, 7]
| Construction time [years] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2 |  | 6
| Space requirement [1000 m2/MW_e] | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.03 | 0.01 | 0.03 | G | 7
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to note
| Secondary regulation (of full load, per minute) [] | 20% | 20% | 20% | 20% | 20% | 50% | 20% | 50% | C | 6
| Minimum load (of full load) [] | 25% | 23% | 20% | 20% | 20% | 25% | 20% | 25% | A | 6
| Warm start-up time [hours] | 0.25 | 0.23 | 0.2 | 0.2 | 0.1 | 0.5 | 0.1 | 0.4 |  | [5, 6, 8]
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 1 | 0.4 | 1 |  | [5, 6, 8]
Environment
SO2 (degree of desulphuring) [] | bar: ctrl to upper
| NOX [g/GJ_i] | 20 | 15 | 10 | 10 | 10 | 30 | 7.5 | 20 | D | [7, 9]
| CH4 [g/GJ_i] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 | G | 9
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 | G | 9
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 0.6 | 0.59 | 0.56 | 0.52 | 0.4 | 0.9 | 0.35 | 0.85 |  | [6, 10]
Nominal investment (equipment) [2015-MEUR/MW_e] | bar: note
Nominal investment (installation) [2015-MEUR/MW_e] | bar: note
| Variable O&M (*total) [2015-EUR/MWh_e] | 4.5 | 4.4 | 4.2 | 4 | 4 | 6 | 3 | 5 |  | 6
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 20000 | 19500 | 18600 | 18000 |  |  |  |  | B | 6
Notes:
A. Very low efficiency at low loads and often increased Nox emisison
B. Insurance excluded, unknown. Daily start assumed
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. Combined with DGC assumptions, CHP configuration
H. GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
I. No data available, no known use
J. Not relevant for this CHP configuration
K. No data available
L. DGC Estimate
M. Air preheating by internal recuperation included
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
5. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
6. Wärtsila Technical Journal "in detail" 02-2014
7. Data specs from maufacturers (Web) 2015
8. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
9. Danish Gas Technology Centre, environmental survey 2012
10. Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
11. IEA: Projected cost of generating electricity, 2010
12. COWI 2015 input
13. The Omes Project results (2005)
14. WBDG-Publication, B. L. Capehart, Microtubines, 2014

## 04 Gas turb. simple cycle Sm-Me
Technology |  | Gas turbine, simple cycle - back pressure - natural gas - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 5; upper: 40; lower: 5; upper: 40; note: F
| Electrical efficiency (net, name plate) [] | 36% | 37% | 39% | 40% | 32% | 40% | 34% | 42% | [G, H] | [6, 12]
| Electrical efficiency (net, annual average) [] | 34% | 35% | 37% | 38% | 30% | 38% | 32% | 40% |  | [6, 11]
| Cb coefficient (50°C/100°C) | 0.71 | 0.73 | 0.8 | 0.8 | 0.61 | 0.8 | 0.7 | 0.9 |  | [6, 12]
Cv coefficient (50°C/100°C) | bar: note
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 3% | 2% | 3% |  | 6
| Planned outage [weeks per year] | 3 | 2.8 | 2.5 | 2.5 | 2 | 3.5 | 1.5 | 3 |  | 6
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | E | [6, 7]
| Construction time [years] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 1.5 | 1 | 1.5 |  | 6
| Space requirement [1000 m2/MW_e] | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.07 | 0.03 | 0.07 | G | 7
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to note
| Secondary regulation (of full load, per minute) [] | 20% | 20% | 20% | 20% | 20% | 50% | 20% | 50% | C | 6
| Minimum load (of full load) [] | 25% | 23% | 20% | 20% | 20% | 25% | 20% | 25% | A | 6
| Warm start-up time [hours] | 0.25 | 0.23 | 0.2 | 0.2 | 0.1 | 0.5 | 0.1 | 0.4 |  | [5, 6, 8]
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 1 | 0.4 | 1 |  | [5, 6, 8]
Environment
SO2 (degree of desulphuring) [] | bar: ctrl to upper
| NOX [g/GJ_i] | 20 | 15 | 10 | 10 | 10 | 30 | 8 | 20 | D | [7, 9]
| CH4 [g/GJ_i] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 |  | 9
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 |  | 9
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 0.75 | 0.73 | 0.7 | 0.68 | 0.6 | 1 | 0.55 | 0.95 |  | [6, 10]
Nominal investment (equipment) [2015-MEUR/MW_e] | bar: note
Nominal investment (installation) [2015-MEUR/MW_e] | bar: note
| Variable O&M (*total) [2015-EUR/MWh_e] | 5.5 | 5.4 | 5.1 | 4.6 | 5 | 7 | 4 | 6 |  | 6
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 20000 | 19500 | 18600 | 18000 |  |  |  |  | B | 6
Notes:
A. Very low efficiency at low loads and often increased Nox emisison
B. Insurance excluded, unknown. Daily start assumed
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. Combined with DGC assumptions, CHP configuration
H. GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
I. No data available, no known use
J. Not relevant for this CHP configuration
K. No data available
L. DGC Estimate
M. Air preheating by internal recuperation included
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
5. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
6. Wärtsila Technical Journal "in detail" 02-2014
7. Data specs from maufacturers (Web) 2015
8. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
9. Danish Gas Technology Centre, environmental survey 2012
10. Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
11. IEA: Projected cost of generating electricity, 2010
12. COWI 2015 input
13. The Omes Project results (2005)
14. WBDG-Publication, B. L. Capehart, Microtubines, 2014

## 04 Gas turb. simple cycle Micro
Technology |  | Gas turbine, simple cycle - back pressure - natural gas - micro
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 0.01; upper: 0.2; lower: 0.01; upper: 0.2
| Electrical efficiency (net, name plate) [] | 30% | 30% | 30% | 30% | 23% | 32% | 25% | 35% | M | 7
| Electrical efficiency (net, annual average) [] | 28% | 28% | 28% | 28% | 21% | 29% | 23% | 33%
| Cb coefficient (50°C/100°C) | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.85 | 0.4 | 0.85 |  | [7, 13]
Cv coefficient (50°C/100°C) | bar: note
Forced outage [] | bar: ctrl to ctrl
Planned outage [weeks per year]
| Technical lifetime [years] | 15 | 15 | 15 | 15 | 10 | 20 | 10 | 20 | L
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.8 | 0.2 | 0.7 | L | 13
| Space requirement [1000 m2/MW_e] | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.15 | 0.05 | 0.15 |  | 7
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
Secondary regulation (of full load, per minute) [] | bar: ctrl to upper
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 30% | 50% | 25% | 50% | L | [7, 13]
| Warm start-up time [hours] | ctrl: 0.25; ctrl: 0.25; ctrl: 0.25; ctrl: 0.25
| Cold start-up time [hours] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5
Environment
| SO2 (degree of desulphuring) [] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | 13
| NOX [g/GJ_i] | 10 | 10 | 10 | 10 | 6 | 15 | 6 | 15 |  | [7, 13]
| CH4 [g/GJ_i] | ctrl: 6; ctrl: 6; ctrl: 6; ctrl: 6; ref: 13
| N2O [g/GJ_i] | ref: 13
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | ctrl: 1.2; ctrl: 1.2; ctrl: 1.1; ctrl: 1; ref: [13, 14]
| Nominal investment (equipment) [2015-MEUR/MW_e] | ctrl: 0.85; ctrl: 0.85; ctrl: 0.8; ctrl: 0.7; ref: [13, 14]
| Nominal investment (installation) [2015-MEUR/MW_e] | ctrl: 0.35; ctrl: 0.35; ctrl: 0.3; ctrl: 0.3; ref: [13, 14]
| Variable O&M (*total) [2015-EUR/MWh_e] | 15 | 15 | 14 | 13 | 10 | 15 | 8 | 15 |  | 13
Fixed O&M (*total) [2015-EUR/MW_e/y]
Notes:
A. Very low efficiency at low loads and often increased Nox emisison
B. Insurance excluded, unknown. Daily start assumed
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. Combined with DGC assumptions, CHP configuration
H. GT's (5 MWe) are available including internal recuperator; the electrical nominal efficiency is then 37 % (LCV basis)
I. No data available, no known use
J. Not relevant for this CHP configuration
K. No data available
L. DGC Estimate
M. Air preheating by internal recuperation included
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
5. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
6. Wärtsila Technical Journal "in detail" 02-2014
7. Data specs from maufacturers (Web) 2015
8. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
9. Danish Gas Technology Centre, environmental survey 2012
10. Smart Power Generation - The future of electricity production, J. Klimstra & M. Hotakainen 2011
11. IEA: Projected cost of generating electricity, 2010
12. COWI 2015 input
13. The Omes Project results (2005)
14. WBDG-Publication, B. L. Capehart, Microtubines, 2014

## 05 Gas turb. CC, steam extract.
Technology |  | Gas turbine, combined cycle - extraction - natural gas - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 100; upper: 500; lower: 100; upper: 500; note: F
| Electrical efficiency (net, name plate) [] | 58% | 59% | 61% | 63% | 55% | 61% | 58% | 65% |  | 5
| Electrical efficiency (net, annual average) [] | 55% | 56% | 58% | 60% | 52% | 58% | 55% | 62% |  | [5, 9]
| Cb coefficient (50°C/100°C) | 1.7 | 1.8 | 2 | 2.2 | 1.5 | 2.2 | 1.5 | 2.4
| Cv coefficient (50°C/100°C) | ctrl: 0.15; ctrl: 0.15; ctrl: 0.15; ctrl: 0.15; note: J
| Forced outage [] | 3% | 3% | 3% | 3% | 2% | 4% | 2% | 4% |  | 5
| Planned outage [weeks per year] | 2.5 | 2.3 | 2 | 2 | 2 | 4 | 2 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | E | [5, 3]
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 5
| Space requirement [1000 m2/MW_e] | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.03 | 0.01 | 0.03 | G | 3
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
| Secondary regulation (of full load, per minute) [] | 15% | 15% | 15% | 15% | 5% | 15% | 5% | 15% |  | [5, 3, 11]
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 30% | 50% | 30% | 50% | A | [5, 3, 11]
| Warm start-up time [hours] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | H | [5, 6, 1, 11]
| Cold start-up time [hours] | 2.5 | 2.5 | 2.5 | 2 | 2 | 5 | 1.5 | 5 |  | [5, 6, 1, 11]
Environment
SO2 (degree of desulphuring) [] | bar: ctrl to upper
| NOX [g/GJ_i] | 20 | 15 | 10 | 8 | 10 | 30 | 5 | 15 | D | [3, 7]
| CH4 [g/GJ_i] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 | G | 7
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 | G | 7
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 0.9 | 0.88 | 0.83 | 0.8 | 0.8 | 1.2 | 0.7 | 1.1 |  | [5, 8]
| Nominal investment (equipment) [2015-MEUR/MW_e] | 0.7 | 0.68 | 0.64 | 0.61 | 0.65 | 1.02 | 0.6 | 0.95 |  | 10
| Nominal investment (installation) [2015-MEUR/MW_e] | 0.2 | 0.2 | 0.19 | 0.19 | 0.15 | 0.18 | 0.1 | 0.15 |  | 10
| Variable O&M (*total) [2015-EUR/MWh_e] | 4.5 | 4.4 | 4.2 | 4 | 3 | 7 | 3 | 7 |  | 5
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 30000 | 29300 | 27800 | 26000 | 25000 | 35000 | 20000 | 30000 | B | 5
Notes:
A. Low efficiency at low loads and often increased NOx emission
B. Limited availability of data
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. CHP configuration, Including DGC assumptions
H. Manufacturers says down to 30 minute
I. No data available
J. Data on Cv from the 2012 version roughly adjusted for higher electricity efficiency
K. No known use
L. No Relevance for Back Pressure Lay Out
M. Upward regulation is typically 10 - 15 %/min, while downward regulation is > 30 % /min
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
3. Data specs from maufacturers (Web) 2015
5. Wärtsila Technical Journal "in detail" 02-2014
6. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
7. Danish Gas Technology Centre, environmental survey 2012
8. Smart Power Generation; the future of electricity production, J. Klimstra & M. Hotakainen 2011
9. IEA: Projected cost of generating electricity, 2010
10. UK Electricity Generation Costs Update, M.M. Donald, June 2010
11. Siemens : Data on GT-CC (2010)

## 05 Gas turb. CC, Back-pressure
Technology |  | Gas turbine, combined cycle - back pressure - natural gas - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 10; upper: 100; lower: 10; upper: 100; note: F
| Electrical efficiency (net, name plate) [] | 50% | 51% | 53% | 55% | 42% | 55% | 45% | 58% |  | 5
| Electrical efficiency (net, annual average) [] | 47% | 48% | 50% | 52% | 39% | 52% | 42% | 55% |  | [5, 9]
| Cb coefficient (50°C/100°C) | 1.2 | 1.3 | 1.4 | 1.55 | 0.9 | 1.6 | 1.1 | 1.7
Cv coefficient (50°C/100°C) | bar: note
| Forced outage [] | 3% | 3% | 3% | 3% | 2% | 4% | 2% | 4% |  | 5
| Planned outage [weeks per year] | 2.5 | 2.3 | 2 | 2 | 2 | 4 | 1.5 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | E | [5, 3]
| Construction time [years] | 2.5 | 2 | 2 | 2 | 2 | 3 | 2 | 3 |  | 5
| Space requirement [1000 m2/MW_e] | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.04 | 0.02 | 0.04 | G | 3
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
| Secondary regulation (of full load, per minute) [] | 15% | 15% | 15% | 15% | 5% | 15% | 5% | 15% | [C, M] | [5, 3, 11]
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 30% | 50% | 30% | 50% | A | [5, 3, 11]
| Warm start-up time [hours] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | H | [5, 6, 1, 11]
| Cold start-up time [hours] | 2.5 | 2.5 | 2.5 | 2 | 2 | 5 | 1.5 | 5 |  | [5, 6, 1, 11]
Environment
SO2 (degree of desulphuring) [] | bar: ctrl to upper
| NOX [g/GJ_i] | 20 | 15 | 10 | 8 | 10 | 30 | 5 | 15 | D | [3, 7]
| CH4 [g/GJ_i] | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 8 | 1 | 8 | G | 7
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 | 0.7 | 1.2 | 0.7 | 1.2 | G | 7
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 1.3 | 1.3 | 1.2 | 1.1 | 1.1 | 1.8 | 0.9 | 1.6 |  | [5, 9]
| Nominal investment (equipment) [2015-MEUR/MW_e] | 1 | 1 | 0.9 | 0.8 | 0.8 | 1.4 | 0.65 | 1.25 |  | 10
| Nominal investment (installation) [2015-MEUR/MW_e] | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.25 | 0.35 |  | 10
| Variable O&M (*total) [2015-EUR/MWh_e] | 4.5 | 4.4 | 4.2 | 4 | 3 | 7 | 3 | 7 |  | 5
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 30000 | 29300 | 27800 | 26000 | 25000 | 35000 | 20000 | 30000 | B | 5
Notes:
A. Low efficiency at low loads and often increased NOx emission
B. Limited availability of data
C. Power related
D. Based on Dry Low NOx (DLN) techniques
E. Technical- and design life most often > 25 years
F. Electrical output
G. CHP configuration, Including DGC assumptions
H. Manufacturers says down to 30 minute
I. No data available
J. Data on Cv from the 2012 version roughly adjusted for higher electricity efficiency
K. No known use
L. No Relevance for Back Pressure Lay Out
M. Upward regulation is typically 10 - 15 %/min, while downward regulation is > 30 % /min
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
3. Data specs from maufacturers (Web) 2015
5. Wärtsila Technical Journal "in detail" 02-2014
6. Danish Gas Technology Centre, analysis and discussion with manufacturers, April 2013
7. Danish Gas Technology Centre, environmental survey 2012
8. Smart Power Generation; the future of electricity production, J. Klimstra & M. Hotakainen 2011
9. IEA: Projected cost of generating electricity, 2010
10. UK Electricity Generation Costs Update, M.M. Donald, June 2010
11. Siemens : Data on GT-CC (2010)

## 06 Gas engines, natural gas
Technology |  | Engine - back pressure - natural gas - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 1; upper: 10; lower: 1; upper: 10
| Electrical efficiency (net, name plate) [] | 46% | 47% | 48% | 50% | 40% | 48% | 44% | 52% | A | [3, 4]
| Electrical efficiency (net, annual average) [] | 44% | 45% | 47% | 48% | 38% | 46% | 42% | 50% | A | [3, 4, 7]
| Cb coefficient (50°C/100°C) | 0.9 | 0.95 | 0.99 | 1.04 | 0.65 | 1.02 | 0.65 | 1.15 |  | [3, 4, 7]
Cv coefficient (50°C/100°C) | bar: note
| Forced outage [] | 3% | 3% | 3% | 3% | 2% | 5% | 2% | 5% |  | [5, 6]
| Planned outage [weeks per year] | 0.8 | 0.8 | 0.8 | 0.8 |  |  |  |  | H | [5, 6]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | D | [4, 5, 7]
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | B | [3, 6]
| Space requirement [1000 m2/MW_e] | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.05 | 0.03 | 0.04
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 25% | 30% | 35% | 50% | 10% | 40% | 25% | 100% |  | 12
| Secondary regulation (of full load, per minute) [] | 25% | 30% | 40% | 50% | 20% | 100% | 25% | 100% | C | [6, 12, 13]
| Minimum load (of full load) [] | 50% | 50% | 50% | 50% | 30% | 50% | 25% | 50% |  | 6
| Warm start-up time [hours] | 0.05 | 0.05 | 0.05 | 0.05 | 0.01 | 0.15 | 0.01 | 0.15 | C | [6, 10]
| Cold start-up time [hours] | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.4 | 0.2 | 0.4 | E | [6, 10]
Environment
| SO2 (degree of desulphuring) [] | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  | 4
| NOX [g/GJ_i] | 75 | 60 | 60 | 60 | 50 | 100 | 50 | 100 |  | 4
| CH4 [g/GJ_i] | 315 | 315 | 280 | 250 | 300 | 400 | 250 | 350 |  | 4
| N2O [g/GJ_i] | ctrl: 0.6; ctrl: 0.6; ctrl: 0.6; ctrl: 0.6; note: H
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 1 | 0.95 | 0.9 | 0.85 | 0.9 | 1.1 | 0.8 | 1.1 |  | [3, 5, 11]
| Nominal investment (equipment) [2015-MEUR/MW_e] | 0.65 | 0.6 | 0.55 | 0.55 |  |  |  |  | H | [3, 5]
| Nominal investment (installation) [2015-MEUR/MW_e] | 0.35 | 0.35 | 0.35 | 0.3 |  |  |  |  | H | [3, 5]
| Variable O&M (*total) [2015-EUR/MWh_e] | 5.4 | 5.4 | 5.1 | 4.9 | 4 | 12 | 4 | 10 | F | [3, 5, 11]
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 10000 | 9750 | 9300 | 8500 | 7000 | 20000 | 6000 | 15000 | F | 5
Notes:
A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
D. Technical- and design life most often > 25 years
E. For a medium size engine; small engines with less thermal mass might be faster
F. When operating 4000 hours a year
G. Only relevant for steam based CHP
H. No data available
I. DGC estimate for years 2030, 2050
J. No known use, data from n-gas engines
K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. ASUE BHKW Kenndata 2014/2015
4. DGC Efficiency and emission test reports
5. DGC analysis, The gas fired cogneration sector, Bilagsrapport 9, Energiforligs analyse 2013
6. Features and parameters of various power plant technologies, Wartsila "In Detail", 02-2014 etc.
7. Dansk Fjernvarme and FDKV reportings from CHP installations, the Dansk Fjernvarme information is from a 2012 suvey for an earlier version of the report
8. Ongoing Sulpur research project at DGC (MUDP)
10. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
11. Blockheizkraftwerke 2013, M.Buller et al, GWF Gas Erdgas, Juni 2014
12. Suppliers association information etc.
13. MAN Turbo Presentation of Gas Engine with fuel switch, 2012

## 06 Gas engines, biogas
Technology |  | Engine - back pressure - biogas - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | lower: 1; upper: 10; lower: 1; upper: 10
| Electrical efficiency (net, name plate) [] | 42% | 43% | 45% | 47% | 38% | 44% | 42% | 48% | A | [3, 4]
| Electrical efficiency (net, annual average) [] | 40% | 41% | 43% | 45% | 36% | 42% | 40% | 46% | A | [3, 4, 7]
| Cb coefficient (50°C/100°C) | 0.82 | 0.86 | 0.92 | 1 | 0.59 | 0.96 | 0.75 | 1.1 |  | [3, 4, 7]
Cv coefficient (50°C/100°C) | bar: note
| Forced outage [] | 3% | 3% | 3% | 3% | 2% | 5% | 2% | 5% |  | [5, 6]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 |  |  |  |  | H | [5, 6]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | D | [4, 5, 7]
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 | B | [3, 6]
| Space requirement [1000 m2/MW_e] | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.05 | 0.03 | 0.05
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 25% | 30% | 40% | 50% | 10% | 40% | 25% | 100% | J | 8
| Secondary regulation (of full load, per minute) [] | 25% | 30% | 40% | 50% | 20% | 100% | 25% | 100% | C | [6, 8, 13]
| Minimum load (of full load) [] | 50% | 50% | 50% | 50% | 30% | 50% | 25% | 50% |  | 6
| Warm start-up time [hours] | 0.05 | 0.05 | 0.05 | 0.05 | 0.01 | 0.15 | 0.01 | 0.15 | C | [6, 10]
| Cold start-up time [hours] | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.4 | 0.2 | 0.4 | E | [6, 10]
Environment
| SO2 (degree of desulphuring) [] |  |  |  |  | 0% | 99.9% | 0% | 99.9% | K | 8
| NOX [g/GJ_i] | 100 | 100 | 100 | 100 | 90 | 120 | 90 | 120 |  | 4
| CH4 [g/GJ_i] | 300 | 300 | 300 | 300 | 300 | 400 | 300 | 400 |  | 4
N2O [g/GJ_i] | bar: ctrl to ctrl; note
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 1 | 0.95 | 0.9 | 0.85 | 0.8 | 1.2 | 0.8 | 1.2 |  | [3, 5, 11]
| Nominal investment (equipment) [2015-MEUR/MW_e] | ctrl: 0.65; ctrl: 0.6; ctrl: 0.55; ctrl: 0.55; ref: [3, 5]
| Nominal investment (installation) [2015-MEUR/MW_e] | ctrl: 0.35; ctrl: 0.35; ctrl: 0.35; ctrl: 0.3; ref: [3, 5]
| Variable O&M (*total) [2015-EUR/MWh_e] | 8 | 7.5 | 7 | 6 | 6 | 13 | 4 | 12 | F | [3, 5, 11]
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 10000 | 9750 | 9300 | 8500 | 7000 | 20000 | 6000 | 15000 | F | 5
Notes:
A. Ref 1, 2 and 3 is used for 2015 values for 3 - 10 MWe engine, 1 MWe engine 4-5 % points less. Ref 4 & 5 is used for predictions for the future years.
B. The construction time given is for a medium size installation; small installations can be erected in a shorter period
C. Engines have been build and demonstrated for short start up < 1 minute for full electrical load. This includes large engines
D. Technical- and design life most often > 25 years
E. For a medium size engine; small engines with less thermal mass might be faster
F. When operating 4000 hours a year
G. Only relevant for steam based CHP
H. No data available
I. DGC estimate for years 2030, 2050
J. No known use, data from n-gas engines
K. Sulphur is removed in the biogas processing, according to manufactures spec. Lower values for biogas from waste water
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. ASUE BHKW Kenndata 2014/2015
4. DGC Efficiency and emission test reports
5. DGC analysis, The gas fired cogneration sector, Bilagsrapport 9, Energiforligs analyse 2013
6. Features and parameters of various power plant technologies, Wartsila "In Detail", 02-2014 etc.
7. Dansk Fjernvarme and FDKV reportings from CHP installations, the Dansk Fjernvarme information is from a 2012 suvey for an earlier version of the report
8. Ongoing Sulpur research project at DGC (MUDP)
10. Danish Gas Technology Centre, analysis on gas engine and gas turbine dynamics, 2013
11. Blockheizkraftwerke 2013, M.Buller et al, GWF Gas Erdgas, Juni 2014
12. Suppliers association information etc.
13. MAN Turbo Presentation of Gas Engine with fuel switch, 2012

## 08 WtE CHP, Large, 40 degree
Technology |  | Waste CHP, 40/80 degree - back pressure - waste - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 51.77 | 51.77 | 53 | 54.91 | 46.98 | 56.44 | 46.98 | 60.65 | [A, B]
| Electrical efficiency (net, annual average) [] | 22.36% | 22.36% | 22.89% | 23.71% | 19% | 25% | 19% | 27% | [A, B, C]
| Electrical efficiency (net, name plate) [] | 23.53% | 23.53% | 24.09% | 24.96% | 21% | 26% | 21% | 28% | [A, B]
| Cb coefficient (40°C/80°C) | 0.3 | 0.3 | 0.31 | 0.32 | 0.27 | 0.32 | 0.27 | 0.35 | [A, B]
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [A, B]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.91% | 2.91% | 2.921% | 2.911% | 2.147% | 3.196% | 1.718% | 3.238% | [A, B]
Forced outage [] | bar: ctrl to upper; ref
| Planned outage [weeks per year] | 2.5 | 2.38 | 2.15 | 1.76 | 2.02 | 2.73 | 1.32 | 2.2 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.77 | 0.77 | 0.75 | 0.73 | 0.66 | 0.89 | 0.55 | 0.91 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to note
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | [F, G]
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | [F, G]
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [F, G]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [F, G]
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 20 | 10 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 7.95 | 7.76 | 7.38 | 6.46 | 6.59 | 9.09 | 4.72 | 8.03 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 4.79 | 4.68 | 4.51 | 3.96 | 3.97 | 5.55 | 2.84 | 4.9 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_e] | 3.16 | 3.08 | 2.86 | 2.5 | 2.62 | 3.54 | 1.87 | 3.12 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_e] | 24.99 | 24.99 | 24.43 | 23.6 | 21.26 | 28.8 | 17.74 | 29.49 | K | 1
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 229000 | 186000 | 174000 | 148000 | 158000 | 218000 | 109000 | 184000 | L | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 80.19% | 80.19% | 79.89% | 79.57% | 76% | 85% | 73% | 87% | [A, B, C]
| Heat efficiency (net, name plate) [] | 79.01% | 79.01% | 78.68% | 78.32% | 74% | 84% | 71% | 86% | [A, B]
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.87 | 1.83 | 1.78 | 1.61 | 1.55 | 2.14 | 1.18 | 2 | N | 1
| Nominal investment (*total) [2015-MEUR/t_i] | 690 | 670 | 650 | 590 | 570 | 790 | 430 | 740 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 1.13 | 1.1 | 1.09 | 0.99 | 0.94 | 1.31 | 0.71 | 1.22 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.74 | 0.72 | 0.69 | 0.62 | 0.62 | 0.83 | 0.47 | 0.78 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_i] | 5.88 | 5.88 | 5.88 | 5.89 | 5 | 6.78 | 4.43 | 7.36 | K | 1
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 54000 | 43900 | 41900 | 37000 | 37300 | 51300 | 27100 | 46000 | L | 1
| Fixed O&M (*total) [2015-EUR/t_i/y] | 19.87 | 16.15 | 15.43 | 13.61 | 13.73 | 18.87 | 9.99 | 16.94 | L | [1, 4]
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | O
| Output of recovered condensate [t/MWh_i] | 0.11 | 0.11 | 0.11 | 0.12 | 0.1 | 0.14 | 0.1 | 0.15 | [D, K]
| Output of recovered condensate [2015-EUR/t_i] | 17.32 | 17.32 | 17.33 | 17.35 | 14.74 | 19.97 | 13.04 | 21.68 | K | [1, 4]
| Incineration capacity [t_i/h] | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, O]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, O]
| Additional heat potential with heat pumps (of thermal input) [] | 4.151% | 4.151% | 4.015% | 3.74% | 1% | 6% | 1% | 6% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 74.7 tph = tonnes per hour (incineration capacity) divided in two, equally sized furnace/boiler units , corresponding to thermal input of 2x110 MW. One common turbine/generator set is foreseen. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, respectively. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised at DH return temperature 40°C and flow 80°C.
C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2030 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2050. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost.
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
O. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 08 WtE CHP, Large, 50 degree
Technology |  | Waste CHP, 50/100 degree - back pressure - waste - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 46.81 | 46.81 | 48.2 | 50.15 | 42.06 | 51.61 | 42.06 | 55.88 | [A, B]
| Electrical efficiency (net, annual average) [] | 20.21% | 20.21% | 20.81% | 21.65% | 17% | 23% | 17% | 25% | [A, B, C]
| Electrical efficiency (net, name plate) [] | 21.28% | 21.28% | 21.91% | 22.79% | 19% | 24% | 19% | 26% | [A, B]
| Cb coefficient (50°C/100°C) | 0.28 | 0.28 | 0.29 | 0.3 | 0.25 | 0.31 | 0.25 | 0.34 | [A, B]
| Cv coefficient (50°C/100°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [A, B]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.957% | 2.957% | 2.967% | 2.953% | 2.185% | 3.224% | 1.748% | 3.265% | [A, B]
Forced outage [] | bar: ctrl to upper; ref
| Planned outage [weeks per year] | 2.5 | 2.38 | 2.15 | 1.76 | 2.02 | 2.73 | 1.32 | 2.2 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.85 | 0.85 | 0.83 | 0.8 | 0.73 | 0.98 | 0.6 | 1 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to note
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | [F, G]
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | [F, G]
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [F, G]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [F, G]
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 20 | 10 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 8.8 | 8.58 | 8.11 | 7.07 | 7.29 | 10.06 | 5.17 | 8.79 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 5.3 | 5.17 | 4.96 | 4.33 | 4.4 | 6.14 | 3.11 | 5.37 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_e] | 3.49 | 3.41 | 3.15 | 2.74 | 2.9 | 3.92 | 2.05 | 3.42 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_e] | 27.28 | 27.28 | 26.52 | 25.54 | 23.11 | 31.7 | 19.04 | 32.15 | K | 1
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 254000 | 206000 | 191000 | 162000 | 175000 | 241000 | 119000 | 202000 | L | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 76.35% | 76.35% | 76.19% | 76.25% | 72% | 85% | 70% | 86% | [A, B, C]
| Heat efficiency (net, name plate) [] | 75.29% | 75.29% | 75.09% | 75.11% | 70% | 84% | 68% | 85% | [A, B]
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.87 | 1.83 | 1.78 | 1.61 | 1.55 | 2.14 | 1.18 | 2 | N | 1
| Nominal investment (*total) [2015-MEUR/t_i] | 690 | 670 | 650 | 590 | 570 | 790 | 430 | 740 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 1.13 | 1.1 | 1.09 | 0.99 | 0.94 | 1.31 | 0.71 | 1.22 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.74 | 0.72 | 0.69 | 0.62 | 0.62 | 0.83 | 0.47 | 0.78 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_i] | 5.8 | 5.8 | 5.81 | 5.82 | 4.92 | 6.74 | 4.34 | 7.33 | K | 1
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 54000 | 43900 | 41900 | 37000 | 37300 | 51300 | 27100 | 46000 | L | 1
| Fixed O&M (*total) [2015-EUR/t_i/y] | 19.87 | 16.15 | 15.43 | 13.61 | 13.73 | 18.87 | 9.99 | 16.94 | L | [1, 4]
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | O
| Output of recovered condensate [t/MWh_i] | 0.03 | 0.03 | 0.04 | 0.05 | 0.01 | 0.11 | 0.01 | 0.11 | [D, K]
| Output of recovered condensate [2015-EUR/t_i] | 17.1 | 17.1 | 17.11 | 17.15 | 14.49 | 19.87 | 12.79 | 21.59 | K | [1, 4]
| Incineration capacity [t_i/h] | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | 74.69 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, O]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, O]
| Additional heat potential with heat pumps (of thermal input) [] | 10.04% | 10.04% | 9.709% | 9.042% | 4% | 12% | 4% | 12% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 74.7 tph = tonnes per hour (incineration capacity) divided in two, equally sized furnace/boiler units , corresponding to thermal input of 2x110 MW. One common turbine/generator set is foreseen. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, respectively. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised at DH return temperature 50°C and flow 100°C.
C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2030 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2050. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost.
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
O. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 08 WtE CHP, Medium
Technology |  | Waste CHP - back pressure - waste - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 18.61 | 18.61 | 19.03 | 19.69 | 16.91 | 20.24 | 16.91 | 21.66 | [A, B]
| Electrical efficiency (net, annual average) [] | 22.1% | 22.1% | 22.6% | 23.38% | 19% | 25% | 19% | 26% | [A, B, C]
| Electrical efficiency (net, name plate) [] | 23.26% | 23.26% | 23.79% | 24.61% | 21% | 26% | 21% | 28% | [A, B, C]
| Cb coefficient (40°C/80°C) | 0.3 | 0.3 | 0.3 | 0.31 | 0.27 | 0.32 | 0.27 | 0.35 | [A, B]
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [A, B]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.91% | 2.91% | 2.922% | 2.911% | 2.147% | 3.196% | 1.718% | 3.268% | [A, B]
Forced outage [] | bar: ctrl to upper; ref
| Planned outage [weeks per year] | 3 | 2.85 | 2.58 | 2.11 | 2.43 | 3.28 | 1.58 | 2.64 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 1.61 | 1.61 | 1.58 | 1.52 | 1.37 | 1.85 | 1.14 | 1.9 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to note
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | [F, G]
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | [F, G]
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [F, G]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [F, G]
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 40 | 10 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 9.25 | 9.02 | 8.6 | 7.54 | 7.67 | 10.59 | 5.5 | 9.37 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 5.62 | 5.48 | 5.31 | 4.66 | 4.66 | 6.52 | 3.34 | 5.78 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_e] | 3.63 | 3.54 | 3.29 | 2.88 | 3.01 | 4.07 | 2.16 | 3.6 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_e] | 25.28 | 25.28 | 24.74 | 23.93 | 21.51 | 29.14 | 17.99 | 29.89 | K | 1
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 298000 | 262000 | 245000 | 209000 | 223000 | 306000 | 154000 | 260000 | L | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 79.99% | 79.99% | 79.71% | 79.42% | 76% | 85% | 73% | 88% | [A, B, C]
| Heat efficiency (net, name plate) [] | 78.82% | 78.82% | 78.52% | 78.19% | 74% | 84% | 71% | 86% | [A, B]
| Nominal investment (*total) [2015-MEUR/MW_i] | 2.15 | 2.1 | 2.05 | 1.86 | 1.78 | 2.46 | 1.35 | 2.31 | N | 1
| Nominal investment (*total) [2015-MEUR/t_i] | 790 | 770 | 750 | 680 | 660 | 910 | 500 | 850 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 1.31 | 1.28 | 1.26 | 1.15 | 1.08 | 1.52 | 0.82 | 1.42 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.84 | 0.82 | 0.78 | 0.71 | 0.7 | 0.95 | 0.53 | 0.88 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_i] | 5.88 | 5.88 | 5.88 | 5.89 | 5 | 6.78 | 4.43 | 7.36 | K | 1
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 69300 | 61000 | 58200 | 51400 | 51900 | 71200 | 37800 | 64000 | L | 1
| Fixed O&M (*total) [2015-EUR/t_i/y] | 25.51 | 22.46 | 21.42 | 18.92 | 19.09 | 26.2 | 13.91 | 23.56 | L | [1, 4]
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | P
| Output of recovered condensate [t/MWh_i] | 0.11 | 0.11 | 0.11 | 0.12 | 0.1 | 0.14 | 0.1 | 0.14 | [D, K]
| Output of recovered condensate [2015-EUR/t_i] | 17.32 | 17.32 | 17.33 | 17.35 | 14.74 | 19.97 | 13.04 | 21.67 | K | [1, 4]
| Incineration capacity [t_i/h] | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | 27.16 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, P]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, P]
| Additional heat potential with heat pumps (of thermal input) [] | 4.151% | 4.151% | 4.015% | 3.74% | 1% | 6% | 1% | 6% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 27.2 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 80 MW. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, restpectively. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised for DH return temperature 40°C and flow 80°C
C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
O. Through a turbine by-pass all the produced steam energy can be used for District Heat production. It can be assumed that all electricity production is converted into heat production in by-pass.
P. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 08 WtE CHP, Small
Technology |  | Waste CHP - back pressure - waste - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 7.96 | 7.96 | 8.12 | 8.34 | 7.25 | 8.62 | 7.25 | 9.19 | [A, B]
| Electrical efficiency (net, annual average) [] | 21.59% | 21.59% | 22.03% | 22.64% | 18% | 24% | 18% | 25% | [A, B, C]
| Electrical efficiency (net, name plate) [] | 22.73% | 22.73% | 23.19% | 23.83% | 20% | 25% | 20% | 27% | [A, B, C]
| Cb coefficient (40°C/80°C) | 0.29 | 0.29 | 0.29 | 0.3 | 0.26 | 0.31 | 0.26 | 0.33 | [A, B]
| Cv coefficient (40°C/80°C) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [A, B]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.91% | 2.91% | 2.922% | 2.939% | 2.147% | 3.229% | 1.718% | 3.3% | [A, B]
Forced outage [] | bar: ctrl to upper; ref
| Planned outage [weeks per year] | 3.5 | 3.33 | 3.01 | 2.46 | 2.83 | 3.83 | 1.85 | 3.08 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 2.51 | 2.51 | 2.46 | 2.4 | 2.14 | 2.89 | 1.8 | 3 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | [F, G]
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | [F, G]
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [F, G]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [F, G]
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 40 | 20 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 10.65 | 10.39 | 9.94 | 8.77 | 8.83 | 12.21 | 6.39 | 10.9 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 6.63 | 6.46 | 6.28 | 5.55 | 5.49 | 7.69 | 3.98 | 6.87 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_e] | 4.03 | 3.93 | 3.66 | 3.22 | 3.34 | 4.52 | 2.42 | 4.03 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_e] | 25.88 | 25.88 | 25.38 | 24.7 | 22.02 | 29.81 | 18.57 | 30.86 | K | 1
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 425000 | 411000 | 382000 | 328000 | 349000 | 478000 | 242000 | 408000 | L | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 80.3% | 80.3% | 80.09% | 80.49% | 77% | 86% | 74% | 88% | [A, B, C]
| Heat efficiency (net, name plate) [] | 79.16% | 79.16% | 78.93% | 79.3% | 75% | 85% | 72% | 86% | [A, B]
| Nominal investment (*total) [2015-MEUR/MW_i] | 2.42 | 2.36 | 2.3 | 2.09 | 2.01 | 2.77 | 1.52 | 2.6 | N | 1
| Nominal investment (*total) [2015-MEUR/t_i] | 890 | 870 | 850 | 770 | 740 | 1020 | 560 | 960 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 1.9 | 1.47 | 1.46 | 1.32 | 1.25 | 1.75 | 0.95 | 1.64 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_i] | 1.16 | 0.89 | 0.85 | 0.77 | 0.76 | 1.03 | 0.58 | 0.96 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_i] | 5.88 | 5.88 | 5.88 | 5.89 | 5 | 6.78 | 4.43 | 7.36 | K | 1
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 96500 | 93400 | 88600 | 78100 | 79400 | 108500 | 57700 | 97300 | L | 1
| Fixed O&M (*total) [2015-EUR/t_i/y] | 35.55 | 34.37 | 32.61 | 28.74 | 29.22 | 39.96 | 21.23 | 35.82 | L | [1, 4]
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | O
| Output of recovered condensate [t/MWh_i] | 0.11 | 0.11 | 0.11 | 0.12 | 0.1 | 0.14 | 0.1 | 0.14 | [D, K]
| Output of recovered condensate [2015-EUR/t_i] | 17.32 | 17.32 | 17.33 | 17.34 | 14.74 | 19.96 | 13.04 | 21.67 | K | [1, 4]
| Incineration capacity [t_i/h] | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, O]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, O]
| Additional heat potential with heat pumps (of thermal input) [] | 4.151% | 4.151% | 4.015% | 3.877% | 1% | 6% | 1% | 6% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 11.9 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 35 MW. Live steam pressure in base case 50 bara, temperature 425 °C of 2015 and 2020, increasing to 440 °C and 450 °C, in 2030 and 2050, respectively. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only) and a back-pressure turbine/condenser system optimised for DH return temperature 40°C and flow 80°C
C. Annual average heat output is higher than nameplate because the total efficiency is constant, and the annual average electricity generation is lower than nameplate electricity output. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
F. Regulation and start-up refer to electricity generation controlled by the turbine operation.The WtE facility would usually be operating at 100% thermal input, and the electricity output is controlled to the desired level by use of turbine by-pass, by which excess steam is used to produce DH-energy. Warm start-up time refers to 2 days down-time of the turbine.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (in stead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream the flue gas treatment system. Sulphur content in fuel 270 g/GJ.
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR using urea injection. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract..
O. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 08 WtE HOP
Technology |  | Waste boiler - boiler - waste - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 36.95 | 36.95 | 37.04 | 37.21 | 36.26 | 37.92 | 36.26 | 38.08 | [A, B]
| Heat efficiency (net, annual average) [] | 105.6% | 105.6% | 105.8% | 106.3% | 103% | 109% | 103% | 109% | [A, B, C]
| Heat efficiency (net, name plate) [] | 105.6% | 105.6% | 105.8% | 106.3% | 103% | 109% | 103% | 109% | [A, B, C]
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.585% | 2.585% | 2.55% | 2.484% | 1.903% | 2.773% | 1.49% | 2.761% | [A, B, C]
Forced outage [] | bar: ctrl to upper; ref
| Planned outage [weeks per year] | 3 | 2.85 | 2.58 | 2.11 | 2.43 | 3.28 | 1.58 | 2.64 | E | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 |  | 1
| Space requirement [1000 m2/MW_h] | 0.54 | 0.54 | 0.54 | 0.54 | 0.46 | 0.62 | 0.4 | 0.67 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) [] | bar: ctrl to note
| Minimum load (of full load) [] | 70% | 70% | 70% | 70% | 70% | 70% | 70% | 70% | G
| Warm start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | G
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | G
Environment
| SO2 (degree of desulphuring) [] | 99.79% | 99.79% | 99.79% | 99.79% | 98.96% | 99.9% | 99.48% | 99.9% | H | 1
| NOX [g/GJ_i] | 80 | 60 | 40 | 20 | 10 | 60 | 10 | 60 | I | [2, 3, 5]
| CH4 [g/GJ_i] | 0.3 | 0.1 | 0.1 | 0.1 | 0 | 0.1 | 0 | 0.1 |  | 2
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | J | 2
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | J | 2
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 1.78 | 1.74 | 1.71 | 1.54 | 1.52 | 2.11 | 1.23 | 2.11 | P
| Nominal investment (equipment) [2015-MEUR/MW_h] | 1.02 | 1 | 1 | 0.91 | 0.87 | 1.23 | 0.71 | 1.23 | P
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.76 | 0.74 | 0.7 | 0.63 | 0.65 | 0.87 | 0.53 | 0.88 | P
| Variable O&M (*total) [2015-EUR/MWh_h] | 7.22 | 7.38 | 8.16 | 8.47 | 6.32 | 8.38 | 6.86 | 10.21 | [K, P]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 1.63 | 1.78 | 2.58 | 2.91 | 1.67 | 1.82 | 2.77 | 3.08 | [K, P]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 5.59 | 5.59 | 5.58 | 5.56 | 4.64 | 6.57 | 4.09 | 7.13 | [K, P]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 80700 | 78000 | 73900 | 64700 | 66800 | 91500 | 49400 | 83500 | P
Technology-specific data
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.88 | 1.84 | 1.81 | 1.64 | 1.6 | 2.22 | 1.31 | 2.24 | N | 1
| Nominal investment (*total) [2015-MEUR/t_i] | 690 | 680 | 660 | 600 | 590 | 820 | 480 | 830 | N | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 1.08 | 1.05 | 1.06 | 0.97 | 0.92 | 1.3 | 0.75 | 1.31 | N | 1
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.8 | 0.78 | 0.74 | 0.67 | 0.68 | 0.92 | 0.56 | 0.93 | M | 1
| Variable O&M (*total) [2015-EUR/MWh_i] | 7.62 | 7.79 | 8.63 | 9 | 6.84 | 8.69 | 7.46 | 10.58 | K | 1
| Variable O&M (electricity cost) [2015-EUR/t_i] | 5.06 | 5.55 | 8.03 | 9.1 | 5.34 | 5.55 | 8.87 | 9.41 | K | [1, 4]
| Variable O&M (other O&M) [2015-EUR/t_i] | 17.39 | 17.39 | 17.4 | 17.42 | 14.81 | 20.04 | 13.11 | 21.75 | K | [1, 4]
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 85200 | 82300 | 78200 | 68800 | 70500 | 96600 | 52600 | 88800 | L | 1
| Fixed O&M (*total) [2015-EUR/t_i/y] | 31.35 | 30.3 | 28.78 | 25.34 | 25.97 | 35.57 | 19.35 | 32.68 | L | [1, 4]
| Output of recovered condensate [t/MWh_i] | 0.13 | 0.13 | 0.14 | 0.14 | 0.12 | 0.17 | 0.12 | 0.17 | [D, K]
| Output of recovered condensate [2015-EUR/t_i] | 22.46 | 22.94 | 25.43 | 26.52 | 20.15 | 25.59 | 21.98 | 31.16 | K | [1, 4]
| Incineration capacity [t_i/h] | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | [A, B]
| Flue gas condensation | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [D, O]
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | [D, O]
| Additional heat potential with heat pumps (of thermal input) [] | 4.151% | 4.151% | 4.015% | 3.74% | 1% | 6% | 1% | 6% | [A, B, D]
Notes:
A. Assumed lower heating value 10.6 MJ/kg, waste input 11.9 tph = tonnes per hour (incineration capacity), corresponding to thermal input of 35 MW. Efficiencies refer to lower heating value.
B. With flue gas condensation (condensation through heat exchange with DH-water, only), DH return temperature 40°C and flow 80°C.
C. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation is included in all cases, and combustion air humidification is included in lower/upper ranges of 2020 and 2050.
E. Focus on availability and ambitions of 2 years' continuous operation is expected to gradually reduce planned outage.
G. The combustion process and boiler may be regulated approx. 1% per minute considering extensive use of inconell (instead of refractory, which may limit rate of change to 0.5% per minute). Minimum load is typically 70% of thermal input under which limit it may be difficult to comply with the requirement of min. 2 sec residence time of the flue gas at min. 850 °C after the last air injection. Below this limit it may also be a challenge to ensure sufficient superheating of the steam. Warm start-up of the combustion process is typically 8 hours and cold start-up is 8 hours.
H. Assumed low SO2-emission 1 g/GJ in 2015 considering the use of flue gas condensation by wet scrubbing down-stream of the flue gas treatment system. Sulphur content in fuel 270 g/GJ
I. Increased focus on NOx reduction is expected in the future, requiring use of SNCR technology to its utmost potential by 2020 (at 60 g/GJ) and use of the more effective catalytic SCR-technology by 2030. The SCR-technology entails additional investment.
J. N2O is expected to be related primarily to the use of SNCR. This is why little N2O is expected when the SCR-deNOx technology is used (indicated by very low NOx-level).
K. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
L. Fixed O&M include amongst other things the major part of staffing and maintenance, analyses, research and development, accounting, insurances, fees, memberships, office. Not included are finance cost, depreciation and amortisation.
M. Installation includes civils works (including waste bunker) and project cost .
N. Assuming LOT-based tendering of electromechanical equipment. EPC contracting is expected at unchanged or slightly higher cost (0-10%), provided only construction is included in the EPC contract.
O. Binary value where 1 = yes and 0 = no
P. Reference to heat output because of the lack of electricity production.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll present work, range of WtE-projects
2. Emission factors of 2006: 102 g/GJ NOx, <8,3 g/GJ for SO2, <0,34 g/GJ for CH4, 1,2 g/GJ for N2O, cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.
3. Environmental permit of a new WtE-facility includes NOx limit value of 180 mg/Nm³ =100 g/GJ. Operation is expected well below limit value. Cf. Miljøstyrelsen, "Tillæg til miljøgodkendelse, Ny ovnlinje 5 på Nordforbrænding, Juni 2013," http://mst.dk/media/mst/Attachments/Tillgtilmiljgodkendelseovn5Juni2013.pdf
4. Two scenarios for adaptation of the waste incineration capacity in Denmark (in Danish: To scenarier for tilpasning af affaldsforbrændingskapaciteten i Danmark.) EA Energianalyse 2014.
5. Best Available Techniques (BAT), Reference Document for Waste Incineration. Frederik Neuwahl, Gianluca Cusano, Jorge Gómez Benavides, Simon Holbrook, Serge Roudier; Best Available Techniques (BAT) Reference Document for Waste Incineration; EUR 29971 EN; doi:10.2760/761437, DEC 2019 https://eippcb.jrc.ec.europa.eu/reference/BREF/WI/JRC118637_WI_Bref_2019_published.pdf

## 09a Wood Chips, Large 40 degree
Technology |  | Biomass CHP, 40/80 degree - back pressure - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 182.24 | 182.62 | 183.28 | 180.08 | 166.32 | 242.89 | 174.4 | 251.01 | A
| Electrical efficiency (net, annual average) [] | 28.85% | 28.92% | 29.02% | 28.51% | 24% | 39% | 26% | 40% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 30.37% | 30.44% | 30.55% | 30.01% | 27% | 41% | 29% | 42% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.37 | 0.37 | 0.38 | 0.37 | 0.34 | 0.5 | 0.35 | 0.51
Cv coefficient (40°C/80°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.962% | 2.941% | 2.943% | 2.935% | 2.181% | 3.272% | 1.799% | 3.432% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.08 | 0.08 | 0.08 | 0.08 | 0.07 | 0.09 | 0.06 | 0.1 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 45% | 45% | 45% | 45% | 45% | 45% | 45% | 45%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [E, G] | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | F | [1, 2, 3]
| NOX [g/GJ_i] | 30 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | F | [1, 2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | [1, 2, 3]
| N2O [g/GJ_i] | 10 | 8 | 6 | 5 | 5 | 10 | 3 | 10 | F | [1, 2, 3]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2, 3]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 3.38 | 3.29 | 3.12 | 2.94 | 2.79 | 3.94 | 2.32 | 4.03 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 2.19 | 2.13 | 2.02 | 1.92 | 1.78 | 2.58 | 1.48 | 2.63 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 1.19 | 1.16 | 1.1 | 1.01 | 1.01 | 1.37 | 0.84 | 1.4 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 4.39 | 4.39 | 4.37 | 4.45 | 3.11 | 4.93 | 2.78 | 5.37 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 97000 | 95000 | 89000 | 84000 | 80000 | 111000 | 64000 | 110000
Technology-specific data
| Heat efficiency (net, annual average) [] | 82.91% | 83.07% | 82.96% | 83.48% | 47% | 87% | 46% | 85% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 81.4% | 81.55% | 81.43% | 81.98% | 44% | 85% | 43% | 83% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.03 | 1 | 0.95 | 0.88 | 0.85 | 1.2 | 0.7 | 1.21 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.66 | 0.65 | 0.62 | 0.58 | 0.54 | 0.78 | 0.44 | 0.79 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.36 | 0.35 | 0.34 | 0.3 | 0.31 | 0.42 | 0.25 | 0.42 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 1.33 | 1.34 | 1.34 | 1.34 | 0.95 | 1.5 | 0.83 | 1.61 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 29500 | 28800 | 27300 | 25100 | 24300 | 33900 | 19100 | 32900
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.22 | 0.22 | 0.22 | 0.22 | 0 | 0.22 | 0 | 0.22 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.869% | 1.869% | 1.87% | 1% | 28% | 1% | 28% | C | 1
Notes:
A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent back-pressure steam turbine without steam re-heat. The system is optimised at DH return temperature 40°C and flow 80°C. At DH return temperature 40 °C and flow 80 °C, for year 2015, the name plate net electricity efficiency increases by about 2.1%-point, to 30.4% and the net name plate heat efficiency is increased about 0.5%-point, to 81.4%, the Cb coefficient increases about 0.02, and the additional heat potential with heat pumps reduced by around 2.7%-point. Other cases experience similar changes.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is particularly low for fluid bed types of plants.
F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF note. The N2O level is relatively high due to the use of a CFB.
G. Warm start is starting with a glowing bed and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09a Wood Chips, Large 50 degree
Technology |  | Biomass CHP, 50/100 degree - back pressure - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 169.53 | 169.84 | 170.47 | 167.48 | 153.68 | 230.21 | 162.19 | 238.75 | A
| Electrical efficiency (net, annual average) [] | 26.84% | 26.89% | 26.99% | 26.52% | 23% | 37% | 24% | 38% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 28.25% | 28.31% | 28.41% | 27.91% | 25% | 39% | 27% | 40% | [A, H] | 1
| Cb coefficient (50°C/100°C) | 0.35 | 0.35 | 0.35 | 0.34 | 0.32 | 0.47 | 0.33 | 0.49
Cv coefficient (50°C/100°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.978% | 2.956% | 2.958% | 2.95% | 2.202% | 3.289% | 1.816% | 3.449% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.09 | 0.09 | 0.09 | 0.09 | 0.08 | 0.1 | 0.07 | 0.11 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 45% | 45% | 45% | 45% | 45% | 45% | 45% | 45%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [E, G] | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | F | [1, 2, 3]
| NOX [g/GJ_i] | 30 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | F | [1, 2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | [1, 2, 3]
| N2O [g/GJ_i] | 10 | 8 | 6 | 5 | 5 | 10 | 3 | 10 | F | [1, 2, 3]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2, 3]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 3.63 | 3.53 | 3.35 | 3.16 | 3 | 4.24 | 2.49 | 4.33 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 2.35 | 2.29 | 2.17 | 2.07 | 1.92 | 2.77 | 1.59 | 2.83 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 1.28 | 1.25 | 1.18 | 1.09 | 1.09 | 1.47 | 0.9 | 1.5 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 4.6 | 4.6 | 4.58 | 4.67 | 3.34 | 5.19 | 2.99 | 5.66 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 105000 | 102000 | 96000 | 90000 | 86000 | 120000 | 69000 | 118000
Technology-specific data
| Heat efficiency (net, annual average) [] | 82.28% | 82.55% | 82.45% | 82.94% | 48% | 86% | 48% | 85% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 80.87% | 81.14% | 81.03% | 81.54% | 46% | 84% | 45% | 83% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.03 | 1 | 0.95 | 0.88 | 0.85 | 1.2 | 0.7 | 1.21 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.66 | 0.65 | 0.62 | 0.58 | 0.54 | 0.78 | 0.44 | 0.79 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.36 | 0.35 | 0.34 | 0.3 | 0.31 | 0.42 | 0.25 | 0.42 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 1.3 | 1.3 | 1.3 | 1.3 | 0.95 | 1.47 | 0.83 | 1.58 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 29500 | 28800 | 27300 | 25100 | 24300 | 33900 | 19100 | 32900
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.19 | 0.19 | 0.19 | 0.19 | 0 | 0.19 | 0 | 0.19 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 4.639% | 4.462% | 4.462% | 4.464% | 4% | 28% | 4% | 28% | C | 1
Notes:
A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent back-pressure steam turbine without steam re-heat. The system is optimised at DH return temperature 50°C and flow 100°C. At DH return temperature 40 °C and flow 80 °C, for year 2015, the name plate net electricity efficiency increases by about 2.1%-point, to 30.4% and the net name plate heat efficiency is increased about 0.5%-point, to 81.4%, the Cb coefficient increases about 0.02, and the additional heat potential with heat pumps reduced by around 2.7%-point. Other cases experience similar changes.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is particularly low for fluid bed types of plants.
F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF note. The N2O level is relatively high due to the use of a CFB.
G. Warm start is starting with a glowing bed and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09a Wood Chips, Medium
Technology |  | Biomass CHP - back pressure - wood chips - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 23.77 | 23.77 | 23.86 | 23.43 | 22.17 | 31.78 | 22.74 | 32.73 | A
| Electrical efficiency (net, annual average) [] | 28.23% | 28.23% | 28.33% | 27.82% | 24% | 38% | 25% | 39% | [A, H, F] | 1
| Electrical efficiency (net, name plate) [] | 29.71% | 29.71% | 29.83% | 29.29% | 27% | 40% | 28% | 41% | [A, H, F] | 1
| Cb coefficient (40°C/80°C) | 0.37 | 0.37 | 0.37 | 0.36 | 0.34 | 0.49 | 0.35 | 0.5
Cv coefficient (40°C/80°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.961% | 2.961% | 2.963% | 2.955% | 2.185% | 3.271% | 1.799% | 3.431% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 0.21 | 0.21 | 0.21 | 0.21 | 0.18 | 0.24 | 0.16 | 0.27
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [E, G] | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | F | [1, 2, 3]
| NOX [g/GJ_i] | 90 | 60 | 40 | 20 | 40 | 60 | 20 | 40 | F | [1, 2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | [1, 2, 3]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2, 3]
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2, 3]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 3.63 | 3.54 | 3.36 | 3.2 | 2.97 | 4.18 | 2.46 | 4.38 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 2.43 | 2.37 | 2.25 | 2.17 | 1.95 | 2.8 | 1.62 | 2.96 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 1.2 | 1.17 | 1.11 | 1.02 | 1.02 | 1.38 | 0.85 | 1.41 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 4.49 | 4.49 | 4.47 | 4.55 | 3.18 | 5.06 | 2.85 | 5.51 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 154000 | 149000 | 140000 | 129000 | 126000 | 173000 | 97000 | 167000
Technology-specific data
| Heat efficiency (net, annual average) [] | 82.72% | 82.72% | 82.61% | 83.15% | 49% | 86% | 46% | 85% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 81.24% | 81.24% | 81.12% | 81.68% | 46% | 84% | 43% | 83% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.08 | 1.05 | 1 | 0.94 | 0.88 | 1.24 | 0.72 | 1.28 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.72 | 0.71 | 0.67 | 0.64 | 0.58 | 0.83 | 0.47 | 0.87 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.36 | 0.35 | 0.33 | 0.3 | 0.3 | 0.41 | 0.25 | 0.41 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 1.33 | 1.33 | 1.33 | 1.33 | 0.95 | 1.5 | 0.83 | 1.61 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 45800 | 44400 | 41800 | 37800 | 37300 | 51500 | 28300 | 48800
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.02 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.22 | 0.22 | 0.22 | 0.22 | 0 | 0.22 | 0 | 0.22 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.944% | 1% | 26% | 1% | 28% | C | 1
Notes:
A. The boiler in the plant is a grate fired boiler producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel. It is to be expected that it is necessary with a specific DeNOx plant (SNCR might not be sufficient). The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy is used for District Heat production.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. It is to be expected that necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 40 g/GJ in which case SCR is used with slight adverse effect on electricity efficiency. From 2017 NOx (and other emissions) must fulfill the BAT_AEL values of the LCP BREF note.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09a Wood Chips, Small
Technology |  | Biomass CHP - back pressure - wood chips - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 2.93 | 2.93 | 2.94 | 2.89 | 2.85 | 2.97 | 2.79 | 2.98 | A
| Electrical efficiency (net, annual average) [] | 13.93% | 13.93% | 13.99% | 13.71% | 12% | 15% | 12% | 15% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 14.66% | 14.66% | 14.72% | 14.43% | 14% | 15% | 13% | 15% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14 | 0.15
Cv coefficient (40°C/80°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.734% | 2.734% | 2.735% | 2.73% | 2.08% | 2.989% | 1.661% | 2.99% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.68 | 0.68 | 0.68 | 0.69 | 0.58 | 0.78 | 0.52 | 0.87
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | D | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | F | [1, 2]
| NOX [g/GJ_i] | 90 | 60 | 40 | 30 | 40 | 80 | 20 | 40 | F | [1, 2]
| CH4 [g/GJ_i] | 20 | 10 | 8 | 4 | 4 | 16 | 2 | 16 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 6.48 | 6.32 | 5.99 | 5.8 | 5.51 | 7.45 | 4.58 | 7.91 | [E, J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 4.02 | 3.92 | 3.72 | 3.7 | 3.42 | 4.63 | 2.84 | 5.01 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 2.45 | 2.39 | 2.27 | 2.09 | 2.09 | 2.82 | 1.73 | 2.89 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 9.26 | 9.26 | 9.22 | 9.41 | 6.45 | 10.41 | 5.78 | 11.35 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 285000 | 281000 | 273000 | 270000 | 241000 | 326000 | 205000 | 347000
Technology-specific data
| Heat efficiency (net, annual average) [] | 97.32% | 97.32% | 97.26% | 97.55% | 73% | 98% | 70% | 98% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 96.58% | 96.58% | 96.52% | 96.82% | 71% | 98% | 69% | 98% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.95 | 0.93 | 0.88 | 0.84 | 0.81 | 1.09 | 0.66 | 1.14 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.59 | 0.58 | 0.55 | 0.53 | 0.5 | 0.68 | 0.41 | 0.72 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.36 | 0.35 | 0.33 | 0.3 | 0.31 | 0.41 | 0.25 | 0.42 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 1.36 | 1.36 | 1.36 | 1.36 | 0.95 | 1.53 | 0.83 | 1.64 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 41800 | 41200 | 40200 | 39000 | 35300 | 47800 | 29600 | 50100
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.02 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0 | 0.25 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.944% | 1% | 26% | 1% | 28% | C | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance. Though, the load control of the heat production is important and most units will perform better than the figure shown. Also, minimum load could be substantially lower.
E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the heat production capacity.
F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
G. Warm start is starting with a glowing fuel layer on the grate.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. Cv=1 describes turbine by-pass operation. During operation the turbine can be by-passed fully or partly for direct district heating production, at operator choice.
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal model and evaluation based on either existing projects, supplier offers, or pre-project studies.
2. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09b Wood Pellets, Large 40 degr
Technology |  | Biomass CHP, 40/80 degree - back pressure - wood pellets - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 267.52 | 268.1 | 268.84 | 268.84 | 262.35 | 348.19 | 262.35 | 348.58 | A
| Electrical efficiency (net, annual average) [] | 31.77% | 31.84% | 31.92% | 31.92% | 29% | 42% | 29% | 42% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 33.44% | 33.51% | 33.6% | 33.6% | 32% | 44% | 32% | 44% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.51 | 0.51 | 0.52 | 0.52 | 0.5 | 0.67 | 0.5 | 0.67
Cv coefficient (40°C/80°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 3.284% | 3.267% | 3.27% | 3.27% | 2.408% | 3.69% | 1.926% | 3.692% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.06 | 0.04 | 0.07
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | G | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | E | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 98.25% | 98.25% | 98.25% | 95.62% | 99.12% | 98.25% | 99.12% |  | [1, 2]
| NOX [g/GJ_i] | 20 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | [C, F] | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 |  | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | [1, 2]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 2.31 | 2.25 | 2.14 | 1.94 | 1.91 | 2.64 | 1.57 | 2.66 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 1.29 | 1.26 | 1.19 | 1.09 | 1.04 | 1.47 | 0.86 | 1.48 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 1.02 | 0.99 | 0.94 | 0.85 | 0.86 | 1.17 | 0.71 | 1.18 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 1.72 | 1.72 | 1.71 | 1.71 | 1.38 | 1.96 | 1.21 | 2.12 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 64000 | 62000 | 59000 | 54000 | 53000 | 72000 | 42000 | 71000
Technology-specific data
| Heat efficiency (net, annual average) [] | 66.82% | 66.94% | 66.85% | 66.85% | 46% | 69% | 46% | 69% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 65.15% | 65.26% | 65.17% | 65.17% | 43% | 67% | 43% | 67% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.77 | 0.75 | 0.72 | 0.65 | 0.64 | 0.89 | 0.53 | 0.89 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.43 | 0.42 | 0.4 | 0.36 | 0.35 | 0.49 | 0.29 | 0.5 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.34 | 0.33 | 0.32 | 0.29 | 0.29 | 0.39 | 0.24 | 0.4 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 0.57 | 0.58 | 0.58 | 0.58 | 0.46 | 0.66 | 0.41 | 0.71 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 21400 | 20900 | 20000 | 18300 | 17600 | 24300 | 14100 | 23900
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0 | 0.06 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.73% | 1.664% | 1.664% | 1.664% | 1% | 13% | 1% | 13% | C | 1
Notes:
A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent steam turbine. Currently, the steam turbine is expected to be a back-pressure turbine with no re-heat. In some of the future scenarios it is assumed that the prices on electricity will allow for an increased electrical efficiency and subsequently re-heating of steam is introduced. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
D. This is given by grid code (Energinet.dk)
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. This plant is equiped with an SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
G. Warm start is starting with the steam system being pressurized.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09b Wood Pellets, Large 50 degr
Technology |  | Biomass CHP, 50/100 degree - back pressure - wood pellets - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 252.95 | 253.44 | 254.15 | 254.15 | 248.11 | 333.42 | 248.11 | 333.79 | A
| Electrical efficiency (net, annual average) [] | 30.04% | 30.1% | 30.18% | 30.18% | 27% | 40% | 27% | 40% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 31.62% | 31.68% | 31.77% | 31.77% | 31% | 42% | 31% | 42% | [A, H] | 1
| Cb coefficient (50°C/100°C) | 0.49 | 0.49 | 0.49 | 0.49 | 0.48 | 0.64 | 0.48 | 0.65
Cv coefficient (50°C/100°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 3.298% | 3.28% | 3.283% | 3.283% | 2.426% | 3.705% | 1.94% | 3.707% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 4.5 | 5.5 | 4 | 5.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.07 | 0.04 | 0.07
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | G | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | E | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 98.25% | 98.25% | 98.25% | 95.62% | 99.12% | 98.25% | 99.12% |  | [1, 2]
| NOX [g/GJ_i] | 20 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | [C, F] | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 |  | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | [1, 2]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 2.44 | 2.38 | 2.26 | 2.05 | 2.02 | 2.79 | 1.66 | 2.81 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 1.36 | 1.33 | 1.26 | 1.15 | 1.1 | 1.56 | 0.91 | 1.56 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 1.08 | 1.05 | 1 | 0.9 | 0.92 | 1.24 | 0.75 | 1.24 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 1.72 | 1.73 | 1.72 | 1.72 | 1.46 | 1.98 | 1.28 | 2.15 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 68000 | 66000 | 63000 | 58000 | 56000 | 77000 | 45000 | 75000
Technology-specific data
| Heat efficiency (net, annual average) [] | 66.14% | 66.37% | 66.28% | 66.28% | 47% | 69% | 47% | 69% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 64.56% | 64.78% | 64.69% | 64.69% | 43% | 67% | 43% | 67% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.77 | 0.75 | 0.72 | 0.65 | 0.64 | 0.89 | 0.53 | 0.89 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.43 | 0.42 | 0.4 | 0.36 | 0.35 | 0.49 | 0.29 | 0.5 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.34 | 0.33 | 0.32 | 0.29 | 0.29 | 0.39 | 0.24 | 0.4 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 0.54 | 0.55 | 0.55 | 0.55 | 0.46 | 0.63 | 0.41 | 0.68 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 21400 | 20900 | 20000 | 18300 | 17600 | 24300 | 14100 | 23900
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.03 | 0.03 | 0.03 | 0.03 | 0 | 0.03 | 0 | 0.03 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 4.13% | 3.973% | 3.972% | 3.972% | 3% | 13% | 3% | 13% | C | 1
Notes:
A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent steam turbine. Currently, the steam turbine is expected to be a back-pressure turbine with no re-heat. In some of the future scenarios it is assumed that the prices on electricity will allow for an increased electrical efficiency and subsequently re-heating of steam is introduced. The system is optimised at DH return temperature 50°C and flow 100°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
D. This is given by grid code (Energinet.dk)
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. This plant is equiped with an SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
G. Warm start is starting with the steam system being pressurized.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09b Wood Pellets, Medium
Technology |  | Biomass CHP - back pressure - wood pellets - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 24.68 | 24.68 | 24.75 | 24.4 | 23.84 | 33.36 | 23.78 | 34.03 | A
| Electrical efficiency (net, annual average) [] | 29.3% | 29.3% | 29.39% | 28.98% | 26% | 40% | 26% | 41% | [A, H, F] | 1
| Electrical efficiency (net, name plate) [] | 30.85% | 30.85% | 30.94% | 30.51% | 29% | 42% | 29% | 43% | [A, H, F] | 1
| Cb coefficient (40°C/80°C) | 0.46 | 0.46 | 0.46 | 0.45 | 0.44 | 0.62 | 0.44 | 0.63
Cv coefficient (40°C/80°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.513% | 2.513% | 2.514% | 2.508% | 1.915% | 2.942% | 1.527% | 3.051% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 0.18 | 0.18 | 0.18 | 0.18 | 0.16 | 0.21 | 0.14 | 0.23
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15%
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 98.25% | 98.25% | 98.25% | 95.62% | 99.12% | 98.25% | 99.12% | F | [1, 2]
| NOX [g/GJ_i] | 80 | 50 | 40 | 20 | 40 | 50 | 10 | 40 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 3.08 | 3.01 | 2.85 | 2.71 | 2.5 | 3.55 | 2.07 | 3.71 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 1.97 | 1.92 | 1.82 | 1.77 | 1.56 | 2.26 | 1.29 | 2.41 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 1.11 | 1.09 | 1.03 | 0.94 | 0.95 | 1.28 | 0.78 | 1.31 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 1.86 | 1.86 | 1.85 | 1.88 | 1.5 | 2.13 | 1.33 | 2.33 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 128000 | 124000 | 117000 | 108000 | 104000 | 144000 | 81000 | 140000
Technology-specific data
| Heat efficiency (net, annual average) [] | 69.23% | 69.23% | 69.14% | 69.57% | 47% | 73% | 45% | 73% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 67.69% | 67.69% | 67.6% | 68.05% | 44% | 71% | 42% | 71% | [A, H, F] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.95 | 0.93 | 0.88 | 0.83 | 0.77 | 1.09 | 0.63 | 1.13 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.61 | 0.59 | 0.56 | 0.54 | 0.48 | 0.7 | 0.39 | 0.73 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.34 | 0.33 | 0.32 | 0.29 | 0.29 | 0.4 | 0.24 | 0.4 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 0.57 | 0.57 | 0.57 | 0.57 | 0.46 | 0.66 | 0.41 | 0.71 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 39500 | 38300 | 36200 | 33100 | 32100 | 44400 | 24600 | 42700
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0 | 0.06 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.729% | 1.729% | 1.729% | 1.73% | 1% | 11% | 1% | 13% | C | 1
Notes:
A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent back pressure steam turbine. It is possible to pulverize wood pellets and use it for suspension firing but it has not been possible to find an appropriate reference. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy is used for District Heat production.
C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. SNCR is assumed at NOx emissions at no less than 40 g/GJ. At lower NOx-levels it is chosen to include a tail-end SCR catalyst with slight adverse effect on electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09b Wood Pellets, Small
Technology |  | Biomass CHP - boiler - wood pellets - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 3.08 | 3.08 | 3.09 | 3.05 | 3 | 3.12 | 2.95 | 3.12 | A
| Electrical efficiency (net, annual average) [] | 14.64% | 14.64% | 14.68% | 14.47% | 13% | 15% | 13% | 15% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 15.41% | 15.41% | 15.46% | 15.23% | 15% | 16% | 14% | 16% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.18 | 0.18 | 0.19 | 0.18 | 0.18 | 0.19 | 0.18 | 0.19
Cv coefficient (40°C/80°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.29% | 2.29% | 2.291% | 2.287% | 1.744% | 2.503% | 1.393% | 2.504% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.49 | 0.49 | 0.49 | 0.49 | 0.41 | 0.56 | 0.37 | 0.62
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | D | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 98.25% | 98.25% | 98.25% | 95.62% | 99.12% | 98.25% | 99.12% | F | 1
| NOX [g/GJ_i] | 90 | 50 | 40 | 30 | 40 | 70 | 20 | 40 | F | 1
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | 1
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 6.22 | 6.06 | 5.75 | 5.54 | 5.28 | 7.15 | 4.38 | 7.55 | [E, J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 4.06 | 3.96 | 3.75 | 3.7 | 3.45 | 4.66 | 2.86 | 5.02 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 2.16 | 2.11 | 2 | 1.83 | 1.84 | 2.49 | 1.52 | 2.54 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 3.89 | 3.89 | 3.88 | 3.94 | 2.99 | 4.43 | 2.67 | 4.84 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 275000 | 271000 | 261000 | 253000 | 232000 | 314000 | 192000 | 325000
Technology-specific data
| Heat efficiency (net, annual average) [] | 84.2% | 84.2% | 84.16% | 84.39% | 74% | 86% | 72% | 86% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 83.43% | 83.43% | 83.39% | 83.62% | 72% | 85% | 71% | 85% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.96 | 0.93 | 0.89 | 0.84 | 0.81 | 1.1 | 0.67 | 1.15 | [E, J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.62 | 0.61 | 0.58 | 0.56 | 0.53 | 0.72 | 0.43 | 0.76 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.33 | 0.32 | 0.31 | 0.28 | 0.28 | 0.38 | 0.23 | 0.39 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 0.6 | 0.6 | 0.6 | 0.6 | 0.46 | 0.68 | 0.41 | 0.74 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 42500 | 41700 | 40300 | 38500 | 35700 | 48400 | 29200 | 49500
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0 | 0.06 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.729% | 1.729% | 1.729% | 1.73% | 1% | 11% | 1% | 13% | C | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper ranges of 2020 and 2050.
E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the thermail input.
F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
G. Warm start is starting with a glowing fuel layer on the grate.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.

## 09c Straw, Large, 40 degree
Technology |  | Biomass CHP, 40/80 degree - back pressure - straw - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 41.59 | 41.59 | 41.72 | 41.72 | 39.48 | 54.62 | 40.62 | 55.84 | A
| Electrical efficiency (net, annual average) [] | 29.94% | 29.94% | 30.03% | 30.03% | 26% | 40% | 27% | 41% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 31.51% | 31.51% | 31.61% | 31.61% | 29% | 42% | 30% | 43% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.45 | 0.45 | 0.46 | 0.46 | 0.43 | 0.6 | 0.44 | 0.61
Cv coefficient (40°C/80°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.838% | 2.838% | 2.84% | 2.84% | 2.091% | 3.137% | 1.729% | 3.298% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.24 | 0.24 | 0.24 | 0.24 | 0.2 | 0.28 | 0.18 | 0.3
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | F | [1, 2]
| NOX [g/GJ_i] | 40 | 30 | 30 | 20 | 20 | 40 | 10 | 30 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 3.46 | 3.38 | 3.21 | 2.91 | 2.86 | 3.97 | 2.35 | 3.99 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 2.14 | 2.09 | 1.98 | 1.8 | 1.73 | 2.45 | 1.43 | 2.46 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_e] | 1.33 | 1.29 | 1.23 | 1.11 | 1.13 | 1.52 | 0.92 | 1.53 | [J, K]
| Variable O&M (*total) [2015-EUR/MWh_e] | 2.11 | 2.11 | 2.1 | 2.1 | 1.62 | 2.4 | 1.42 | 2.58 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 126000 | 122000 | 115000 | 103000 | 103000 | 142000 | 79000 | 133000 | J
Technology-specific data
| Heat efficiency (net, annual average) [] | 70.93% | 70.93% | 70.83% | 70.83% | 48% | 74% | 47% | 73% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 69.35% | 69.35% | 69.25% | 69.25% | 45% | 72% | 44% | 71% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.09 | 1.07 | 1.01 | 0.92 | 0.9 | 1.25 | 0.74 | 1.26 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.67 | 0.66 | 0.63 | 0.57 | 0.55 | 0.77 | 0.45 | 0.78 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.42 | 0.41 | 0.39 | 0.35 | 0.36 | 0.48 | 0.29 | 0.48 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 0.66 | 0.66 | 0.66 | 0.66 | 0.51 | 0.76 | 0.45 | 0.82 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 39700 | 38500 | 36300 | 32400 | 32500 | 44600 | 24900 | 41900 | J
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.06 | 0.06 | 0.06 | 0.05 | 0.06 | 0.07 | 0.05 | 0.08 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.09 | 0.09 | 0.09 | 0.09 | 0 | 0.09 | 0 | 0.09 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.768% | 1.768% | 1.768% | 1.768% | 1% | 15% | 1% | 15% | C | 1
Notes:
A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09c Straw, Large, 50 degree
Technology |  | Biomass CHP, 50/100 degree - back pressure - straw - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 38.99 | 38.99 | 39.11 | 39.11 | 36.88 | 52.01 | 38.07 | 53.28 | A
| Electrical efficiency (net, annual average) [] | 28.06% | 28.06% | 28.15% | 28.15% | 25% | 38% | 25% | 39% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 29.54% | 29.54% | 29.63% | 29.63% | 27% | 40% | 28% | 41% | [A, H] | 1
| Cb coefficient (50°C/100°C) | 0.43 | 0.43 | 0.43 | 0.43 | 0.41 | 0.57 | 0.42 | 0.59
Cv coefficient (50°C/100°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.855% | 2.855% | 2.857% | 2.857% | 2.115% | 3.156% | 1.747% | 3.316% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 3 | 3 | 3 | 3 | 2.5 | 3.5 | 2 | 3.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.26 | 0.26 | 0.26 | 0.26 | 0.22 | 0.29 | 0.19 | 0.32
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | F | [1, 2]
| NOX [g/GJ_i] | 40 | 30 | 30 | 20 | 20 | 40 | 10 | 30 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 3.7 | 3.61 | 3.42 | 3.11 | 3.05 | 4.24 | 2.5 | 4.26 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 2.28 | 2.23 | 2.12 | 1.92 | 1.85 | 2.61 | 1.52 | 2.62 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_e] | 1.41 | 1.38 | 1.31 | 1.18 | 1.2 | 1.63 | 0.98 | 1.63 | [J, K]
| Variable O&M (*total) [2015-EUR/MWh_e] | 2.14 | 2.14 | 2.14 | 2.14 | 1.73 | 2.46 | 1.52 | 2.65 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 134000 | 130000 | 123000 | 109000 | 110000 | 151000 | 84000 | 142000 | J
Technology-specific data
| Heat efficiency (net, annual average) [] | 70.35% | 70.35% | 70.26% | 70.26% | 49% | 73% | 49% | 72% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 68.87% | 68.87% | 68.77% | 68.77% | 47% | 71% | 46% | 70% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.09 | 1.07 | 1.01 | 0.92 | 0.9 | 1.25 | 0.74 | 1.26 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.67 | 0.66 | 0.63 | 0.57 | 0.55 | 0.77 | 0.45 | 0.78 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.42 | 0.41 | 0.39 | 0.35 | 0.36 | 0.48 | 0.29 | 0.48 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 0.63 | 0.63 | 0.63 | 0.63 | 0.51 | 0.73 | 0.45 | 0.79 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 39700 | 38500 | 36300 | 32400 | 32500 | 44600 | 24900 | 41900 | J
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.06 | 0.06 | 0.06 | 0.05 | 0.06 | 0.07 | 0.05 | 0.08 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Output of recovered condensate [t/MWh_i] | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0 | 0.06 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 4.22% | 4.22% | 4.22% | 4.22% | 4% | 15% | 4% | 15% | C | 1
Notes:
A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. The system is optimised at DH return temperature 50°C and flow 100°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09c Straw, Medium
Technology |  | Biomass CHP - back pressure - straw - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 25.29 | 25.29 | 25.36 | 24.99 | 23.67 | 25.72 | 24.33 | 25.84 | A
| Electrical efficiency (net, annual average) [] | 30.03% | 30.03% | 30.12% | 29.68% | 26% | 31% | 27% | 31% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 31.61% | 31.61% | 31.71% | 31.24% | 29% | 33% | 30% | 33% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.46 | 0.46 | 0.46 | 0.45 | 0.43 | 0.47 | 0.44 | 0.47
Cv coefficient (40°C/80°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.847% | 2.847% | 2.849% | 2.84% | 2.091% | 3.168% | 1.728% | 3.211% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 4 | 4 | 4 | 4 | 3.4 | 4.6 | 3 | 5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 1.5 | 3 |  | 1
| Space requirement [1000 m2/MW_e] | 0.28 | 0.28 | 0.28 | 0.28 | 0.24 | 0.32 | 0.21 | 0.35
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | F | [1, 2]
| NOX [g/GJ_i] | 90 | 70 | 50 | 30 | 20 | 90 | 10 | 50 | F | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | [1, 2]
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | [1, 2]
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 3.66 | 3.57 | 3.39 | 3.21 | 3 | 4.31 | 2.58 | 4.39 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 2.22 | 2.16 | 2.05 | 1.98 | 1.77 | 2.64 | 1.56 | 2.7 | [J, K] | 1
| Nominal investment (installation) [2015-MEUR/MW_e] | 1.45 | 1.41 | 1.34 | 1.23 | 1.23 | 1.66 | 1.02 | 1.7 | [J, K] | 1
| Variable O&M (*total) [2015-EUR/MWh_e] | 2.1 | 2.1 | 2.09 | 2.12 | 1.61 | 2.39 | 1.44 | 2.61 | L | 1
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 147000 | 143000 | 134000 | 124000 | 120000 | 168000 | 95000 | 160000 | J | 1
Technology-specific data
| Heat efficiency (net, annual average) [] | 70.21% | 70.21% | 70.11% | 70.57% | 56% | 74% | 56% | 73% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 68.63% | 68.63% | 68.52% | 69.01% | 53% | 72% | 53% | 71% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.16 | 1.13 | 1.07 | 1 | 0.95 | 1.36 | 0.81 | 1.37 | [J, K] | 1
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.46 | 0.45 | 0.42 | 0.38 | 0.39 | 0.53 | 0.32 | 0.53 | K
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.7 | 0.68 | 0.65 | 0.62 | 0.56 | 0.84 | 0.49 | 0.84 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 0.66 | 0.66 | 0.66 | 0.66 | 0.51 | 0.76 | 0.45 | 0.82 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 46600 | 45200 | 42600 | 38700 | 38000 | 53000 | 29600 | 49900 | J
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.08 | 0.05 | 0.08 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.09 | 0.09 | 0.09 | 0.09 | 0 | 0.09 | 0 | 0.09 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.767% | 1.767% | 1.767% | 1.768% | 1% | 15% | 1% | 15% | C | 1
Notes:
A. The boiler in the plant is grate fired producing steam to be used in a subsequent back pressure steam turbine. Though a grate is reasonable flexible with respect to combusting different fuels the fuel feed system will be dependent on the type of fuel used. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Through a turbine by-pass all the produced steam energy can be used for District Heat production.
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance since load will normally follow heat consumption.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. For NOx-emissions no lower than 40 g/GJ SNCR is assumed. It is probably necessary to include a tail-end SCR catalyst to fulfill expected BREF requirements, particularly after year 2030. This has slight adverse effect on the electricity efficiency.
G. Warm start is starting with a glowing fuel layer on the grate and a warm deaerator.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 09c Straw, Small
Technology |  | Biomass CHP - back pressure - straw - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 3.05 | 3.05 | 3.06 | 3.01 | 2.97 | 3.09 | 2.92 | 3.04 | A
| Electrical efficiency (net, annual average) [] | 14.49% | 14.49% | 14.53% | 14.3% | 13% | 15% | 13% | 15% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 15.25% | 15.25% | 15.3% | 15.06% | 14% | 16% | 14% | 16% | [A, H] | 1
| Cb coefficient (40°C/80°C) | 0.18 | 0.18 | 0.18 | 0.18 | 0.17 | 0.18 | 0.17 | 0.18
Cv coefficient (40°C/80°C) | bar: ctrl to note
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.373% | 2.373% | 2.374% | 2.37% | 1.807% | 2.594% | 1.443% | 2.59% |  | 1
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 4 | 4 | 4 | 4 | 3.4 | 4.6 | 3 | 5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.98 | 0.98 | 0.98 | 1 | 0.84 | 1.13 | 0.75 | 1.25
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | D | 1
| Minimum load (of full load) [] | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | D | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | G | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | F | 1
| NOX [g/GJ_i] | 90 | 70 | 50 | 40 | 50 | 90 | 40 | 50 | F | 1
| CH4 [g/GJ_i] | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | F | 1
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | F | 1
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | 1
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 6.85 | 6.68 | 6.34 | 6.09 | 5.83 | 7.88 | 5.09 | 8.31 | [E, J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 3.87 | 3.77 | 3.58 | 3.55 | 3.29 | 4.45 | 2.99 | 4.81 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 2.98 | 2.91 | 2.76 | 2.54 | 2.54 | 3.43 | 2.1 | 3.5 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 4.52 | 4.52 | 4.5 | 4.57 | 3.34 | 5.12 | 2.99 | 5.58 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 318000 | 313000 | 302000 | 293000 | 268000 | 362000 | 227000 | 375000 | J
Technology-specific data
| Heat efficiency (net, annual average) [] | 86.34% | 86.34% | 86.29% | 86.53% | 73% | 88% | 72% | 88% | [B, H] | 1
| Heat efficiency (net, name plate) [] | 85.58% | 85.58% | 85.53% | 85.78% | 72% | 87% | 71% | 87% | [B, H] | 1
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.04 | 1.02 | 0.97 | 0.92 | 0.89 | 1.2 | 0.77 | 1.25 | [E, J, K] | 1
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.46 | 0.44 | 0.42 | 0.38 | 0.39 | 0.52 | 0.32 | 0.53 | K
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.59 | 0.58 | 0.55 | 0.53 | 0.5 | 0.68 | 0.45 | 0.72 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 0.69 | 0.69 | 0.69 | 0.69 | 0.51 | 0.78 | 0.45 | 0.84 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 48600 | 47700 | 46100 | 44100 | 40800 | 55300 | 34200 | 56500 | J
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.08 | 0.08 | 0.07 | 0.07 | 0.07 | 0.09 | 0.06 | 0.09 | K
| Steam reheat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Output of recovered condensate [t/MWh_i] | 0.09 | 0.09 | 0.09 | 0.09 | 0 | 0.09 | 0 | 0.09 | [C, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [C, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.767% | 1.767% | 1.767% | 1.768% | 1% | 14% | 1% | 15% | C | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The electric power is produced by an ORC module (Organic Rankine Cycle; Waste Heat Recovery - WHR). Refer for instance to the following link for further information about technology and suppliers: http://www.enova.no/upload_images/36AC689098414B05A7112FA2EE985BDA.pdf . This is low temperature and low efficiency electric power but at an affordable price. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
D. Secondary regulation normally relates to power production; for this type of plant it may not be of importance. Though, the load control of the heat production is important and most units will perform better than the figure shown. Also, minimum load could be substantially lower.
E. Since electricity generation is only a secondary objective for minor heat producers, it may make more sense to relate the total investment only to the heat production capacity.
F. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
G. Warm start is starting with a glowing fuel layer on the grate.
H. The total efficiency is the sum of electricity efficiency and heat efficiency, applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to turbine outages and other incidents. The resulting lost power production is recovered as heat. This is why "annual average" heat efficiency is higher than "name plate" heat. Efficiencies refer to lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value does not exist for plants with a back pressure turbine or an ORC turbine
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Electricity consumption is not included for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies. NOTICE: There are to our knowledge no references on ORC plants running on straw.

## 09a Wood Chips HOP, small
Technology |  | Biomass boiler - boiler - wood chips - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 6.84 | 6.84 | 6.84 | 6.84 | 5.34 | 6.86 | 5.34 | 6.87 | A | 1
| Heat efficiency (net, annual average) [] | 114% | 114% | 114% | 114% | 89% | 115% | 89% | 115% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 114% | 114% | 114% | 114% | 89% | 115% | 89% | 115% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.216% | 2.216% | 2.216% | 2.216% | 2.114% | 2.472% | 1.691% | 2.47% | [C, K]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_h] | 0.22 | 0.22 | 0.22 | 0.22 | 0.19 | 0.25 | 0.16 | 0.27
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | E | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | H | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 89.85% | 98.98% | 97.97% | 98.98% | G | 1
| NOX [g/GJ_i] | 90 | 60 | 50 | 40 | 40 | 80 | 30 | 40 | I | 2
| CH4 [g/GJ_i] | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | I | 2
| N2O [g/GJ_i] | 4 | 3 | 3 | 1 | 1 | 4 | 1 | 4 | I | 2
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | I | 2
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.71 | 0.69 | 0.66 | 0.59 | 0.6 | 0.81 | 0.49 | 0.82 | [F, L]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.41 | 0.4 | 0.38 | 0.34 | 0.35 | 0.47 | 0.28 | 0.47 | [F, L]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.3 | 0.29 | 0.28 | 0.25 | 0.25 | 0.34 | 0.21 | 0.35 | [F, L]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.59 | 2.72 | 3.43 | 3.78 | 2.34 | 3.71 | 3.29 | 5.22 | M
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 1.4 | 1.53 | 2.24 | 2.59 | 1.51 | 1.99 | 2.56 | 3.38 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1.19 | 1.19 | 1.19 | 1.19 | 0.83 | 1.72 | 0.73 | 1.84 | M
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 33000 | 32500 | 31500 | 29600 | 27800 | 37700 | 22800 | 38000
Technology-specific data
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.81 | 0.79 | 0.75 | 0.68 | 0.69 | 0.93 | 0.56 | 0.94 | [J, L] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.47 | 0.46 | 0.43 | 0.39 | 0.4 | 0.54 | 0.32 | 0.54 | L
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.34 | 0.33 | 0.32 | 0.29 | 0.29 | 0.39 | 0.24 | 0.39 | L
| Variable O&M (*total) [2015-EUR/MWh_i] | 2.95 | 3.1 | 3.91 | 4.31 | 2.68 | 3.3 | 3.77 | 4.65 | M
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 37700 | 37100 | 35900 | 33700 | 31700 | 42900 | 26000 | 43300
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.02 | L
| Output of recovered condensate [t/MWh_i] | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0 | 0.25 | D
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.943% | 1% | 26% | 1% | 26% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E. Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
F. Reference to heat output because of the lack of electricity production
G. Assuming content of sulphur in fuel of 20 g/GJ
H. Warm start is starting with a glowing fuel layer on the grate.
I. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
J. The nominal investment is in the range 0.6 to 1.1 MEUR/MWth
K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09a Wood Chips HOP, medium
Technology |  | Biomass boiler - boiler - wood chips - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 51.64 | 51.64 | 51.64 | 51.64 | 40.38 | 51.81 | 39.66 | 51.86 | A | 1
| Heat efficiency (net, annual average) [] | 114.8% | 114.8% | 114.8% | 114.7% | 89% | 116% | 88% | 116% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 114.8% | 114.8% | 114.8% | 114.7% | 89% | 116% | 88% | 116% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.204% | 2.204% | 2.204% | 2.203% | 2.098% | 2.459% | 1.709% | 2.455% | [C, K]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2 | 2 | 2 | 2 | 1.5 | 2.5 | 1.5 | 2.5 |  | 1
| Space requirement [1000 m2/MW_h] | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.07 | 0.04 | 0.07
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | H | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | G | 1
| NOX [g/GJ_i] | 90 | 60 | 40 | 30 | 40 | 80 | 20 | 40 | I | 2
| CH4 [g/GJ_i] | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | I | 2
| N2O [g/GJ_i] | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | I | 2
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | I | 2
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.51 | 0.49 | 0.47 | 0.45 | 0.43 | 0.58 | 0.35 | 0.62 | [F, L]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.37 | 0.36 | 0.34 | 0.34 | 0.31 | 0.43 | 0.26 | 0.46 | [F, L]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.14 | 0.13 | 0.13 | 0.11 | 0.12 | 0.16 | 0.09 | 0.16 | [F, L]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.57 | 2.7 | 3.41 | 3.76 | 2.33 | 3.68 | 3.27 | 5.27 | M
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 1.39 | 1.52 | 2.23 | 2.58 | 1.5 | 1.98 | 2.55 | 3.41 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1.18 | 1.18 | 1.18 | 1.18 | 0.82 | 1.7 | 0.72 | 1.86 | M
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 42800 | 42000 | 40500 | 38200 | 35800 | 48500 | 28800 | 48500
Technology-specific data
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.58 | 0.57 | 0.54 | 0.52 | 0.49 | 0.67 | 0.4 | 0.71 | L | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.42 | 0.41 | 0.39 | 0.39 | 0.36 | 0.49 | 0.3 | 0.53 | L
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.16 | 0.15 | 0.14 | 0.13 | 0.13 | 0.18 | 0.11 | 0.18 | L
| Variable O&M (*total) [2015-EUR/MWh_i] | 2.95 | 3.1 | 3.91 | 4.32 | 2.68 | 3.3 | 3.77 | 4.65 | M
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 49100 | 48200 | 46400 | 43900 | 41100 | 55600 | 33000 | 55700
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.02 | 0.02 | 0.02 | 0.01 | 0.01 | 0.02 | 0.01 | 0.02 | L
| Output of recovered condensate [t/MWh_i] | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0 | 0.25 | D
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.944% | 1% | 26% | 1% | 28% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate as the basis assumption. Fluid-bed combustion technology may be an alternative.It can be assumed that the data for this does not differ significantly from grate fired boilers. Data in this sheet is applicable for plants in the range of 30-49,9 MW fired capacity (heat input). The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers larger than approx. 20 MW fuel input for hot water production are designed-for-purpose products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E. Load control of the heat production is important and units of this size can make rapid load variations.
F. Reference to heat output because of the lack of electricity production
G. assuming content of sulphur in fuel of 20 g/GJ
H. Warm start is starting with a glowing fuel layer on the grate.
I. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed.
K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplierand operator information, or pre-project studies.
2. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09a Wood Chips HOP, large
Technology |  | Biomass boiler - boiler - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 103.43 | 103.43 | 103.43 | 103.42 | 80.92 | 103.78 | 79.47 | 103.87 | A | 1
| Heat efficiency (net, annual average) [] | 114.9% | 114.9% | 114.9% | 114.9% | 89% | 116% | 88% | 116% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 114.9% | 114.9% | 114.9% | 114.9% | 89% | 116% | 88% | 116% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.201% | 2.201% | 2.201% | 2.2% | 2.095% | 2.456% | 1.706% | 2.452% | [C, K]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 1.7 | 2.3 | 1.5 | 2.5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | 1
| Space requirement [1000 m2/MW_h] | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.06 | 0.04 | 0.06
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | H | 1
| Cold start-up time [hours] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.97% | 97.97% | 97.97% | 97.97% | 94.92% | 98.98% | 97.97% | 98.98% | G | 1
| NOX [g/GJ_i] | 90 | 60 | 40 | 20 | 40 | 60 | 20 | 40 |  | [2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 |  | 3
| N2O [g/GJ_i] | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 |  | 3
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | 3
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.45 | 0.44 | 0.42 | 0.4 | 0.38 | 0.52 | 0.31 | 0.55 | [F, L]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.34 | 0.33 | 0.31 | 0.31 | 0.29 | 0.39 | 0.24 | 0.42 | [F, L]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.11 | 0.11 | 0.1 | 0.09 | 0.09 | 0.13 | 0.08 | 0.13 | [F, L]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.57 | 2.7 | 3.41 | 3.76 | 2.32 | 3.67 | 3.27 | 5.26 | M
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 1.39 | 1.52 | 2.22 | 2.57 | 1.5 | 1.98 | 2.55 | 3.41 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1.18 | 1.18 | 1.18 | 1.18 | 0.82 | 1.7 | 0.72 | 1.86 | M
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 35200 | 34600 | 33300 | 31400 | 29500 | 39900 | 23600 | 39900
Technology-specific data
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.52 | 0.5 | 0.48 | 0.46 | 0.44 | 0.6 | 0.36 | 0.63 | L | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.39 | 0.38 | 0.36 | 0.36 | 0.33 | 0.45 | 0.27 | 0.48 | L
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.13 | 0.12 | 0.12 | 0.11 | 0.11 | 0.15 | 0.09 | 0.15 | L
| Variable O&M (*total) [2015-EUR/MWh_i] | 2.95 | 3.1 | 3.91 | 4.32 | 2.68 | 3.3 | 3.77 | 4.65 | M
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 40500 | 39700 | 38200 | 36100 | 33900 | 45900 | 27200 | 45800
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.02 | L
| Output of recovered condensate [t/MWh_i] | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0.25 | 0 | 0.25 | D
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Additional heat potential with heat pumps (of thermal input) [] | 1.943% | 1.943% | 1.943% | 1.944% | 1% | 26% | 1% | 28% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. Fluid-bed combustion technology may be an alternative. It can be assumed that the data for this does not differ significantly from grate fired boilers. Data in this sheet is applicable for plants in the range of 80-99,9 MW fired capacity (heat input). The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers larger than approx. 20 MW fuel input for hot water production are designed-for-purpose products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. Efficiencies refer to lower heating value. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency. Direct condensation and combustion air humidification are included in all cases except in lower range of 2020 and 2050. The colder the return temperature of the district heating, the higher the total efficiency at direct condensation.
D. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E. Load control of the heat production is important and units of this size can make rapid load variations.
F. Reference to heat output because of the lack of electricity production
G. Assuming content of sulphur in fuel of 20 g/GJ
H. Warm start is starting with a glowing fuel layer on the grate.
K. Result of model calculation, there are reports of DH plants operating at lower power consumption, down to 1% of heat generation.
L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09b Wood Pellets HOP
Technology |  | Biomass boiler - boiler - wood pellets - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 6.07 | 6.07 | 6.07 | 6.07 | 5.45 | 6.09 | 5.37 | 6.1 | A | 1
| Heat efficiency (net, annual average) [] | 101.2% | 101.2% | 101.2% | 101.2% | 90% | 102% | 89% | 102% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 101.2% | 101.2% | 101.2% | 101.2% | 90% | 102% | 89% | 102% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.055% | 2.055% | 2.055% | 2.055% | 1.705% | 2.295% | 1.384% | 2.292% | [C, K]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.55 | 3.45 | 2.25 | 3.75
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_h] | 0.16 | 0.16 | 0.16 | 0.16 | 0.14 | 0.19 | 0.12 | 0.21
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | E | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | H | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 98.25% | 98.25% | 98.25% | 98.25% | 91.25% | 99.12% | 98.25% | 99.12% | G | 1
| NOX [g/GJ_i] | 90 | 50 | 40 | 40 | 40 | 70 | 20 | 40 | G | 1
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G | 1
| N2O [g/GJ_i] | 1.2 | 1 | 1 | 1 | 1 | 3 | 0 | 1 | G | 1
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | G | 1
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.73 | 0.71 | 0.68 | 0.61 | 0.62 | 0.84 | 0.51 | 0.9 | [F, L]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.44 | 0.43 | 0.41 | 0.37 | 0.38 | 0.51 | 0.31 | 0.57 | [F, L]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.29 | 0.28 | 0.27 | 0.24 | 0.24 | 0.33 | 0.2 | 0.33 | [F, L]
| Variable O&M (*total) [2015-EUR/MWh_h] | 1.84 | 1.96 | 2.62 | 2.95 | 1.81 | 2.3 | 2.74 | 3.52 | [F, M]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 1.29 | 1.42 | 2.08 | 2.4 | 1.4 | 1.61 | 2.37 | 2.77 | [F, M]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 0.54 | 0.54 | 0.54 | 0.54 | 0.41 | 0.69 | 0.36 | 0.75 | [F, M]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 33600 | 32700 | 31000 | 27900 | 28000 | 37900 | 21700 | 37100 | F
Technology-specific data
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.74 | 0.72 | 0.69 | 0.62 | 0.63 | 0.85 | 0.52 | 0.91 | [J, L] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.45 | 0.44 | 0.42 | 0.38 | 0.38 | 0.52 | 0.31 | 0.57 | L
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.29 | 0.28 | 0.27 | 0.24 | 0.25 | 0.34 | 0.2 | 0.34 | L
| Variable O&M (*total) [2015-EUR/MWh_i] | 1.86 | 1.98 | 2.65 | 2.98 | 1.84 | 2.09 | 2.78 | 3.15 | M
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 34000 | 33100 | 31300 | 28300 | 28300 | 38300 | 21900 | 37500
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | L
| Output of recovered condensate [t/MWh_i] | 0.06 | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0 | 0.06 | D
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, N]
| Additional heat potential with heat pumps (of thermal input) [] | 1.729% | 1.729% | 1.729% | 1.729% | 1% | 11% | 1% | 13% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate. The system is optimised at DH return temperature 40°C and flow 80°C.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
D. Since wood pellets are relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050.
E. Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
F. Reference to heat output because of the lack of electricity production
G. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However to reach NOx-levels below 40 g/GJ SCR is assumed.
I. Warm start is starting with a glowing fuel layer on the grate.
J. The nominal investment is in the range 0.6 to 1.1 MEUR/Mwth
K. Result of model calculation, there are reports of DH plants operating at lower power consumption
L. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
M. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
N. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.

## 09c Straw HOP
Technology |  | Biomass boiler - boiler - straw - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 6.19 | 6.19 | 6.19 | 6.19 | 5.34 | 6.22 | 5.34 | 6.22 | A | 1
| Heat efficiency (net, annual average) [] | 103.2% | 103.2% | 103.2% | 103.2% | 88% | 104% | 88% | 104% | [B, C] | 1
| Heat efficiency (net, name plate) [] | 103.2% | 103.2% | 103.2% | 103.2% | 88% | 104% | 88% | 104% | [B, C] | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.096% | 2.096% | 2.096% | 2.096% | 1.81% | 2.338% | 1.448% | 2.336% | [C, J]
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 4 | 4 | 4 | 4 | 3.4 | 4.6 | 3 | 5
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 20 | 35 | 20 | 35 |  | 1
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.28 | 0.18 | 0.3
Regulation ability
Primary regulation (of full load, per 30 seconds) []
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | E | 1
| Minimum load (of full load) [] | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | E | 1
| Warm start-up time [hours] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | H | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 95.45% | 96.36% | 99.09% | 99.82% | 90.9% | 99.82% | 95.45% | 99.91% | G | 1
| NOX [g/GJ_i] | 90 | 70 | 70 | 70 | 40 | 90 | 20 | 70 | G | 1
| CH4 [g/GJ_i] | 16 | 11 | 8 | 4 | 4 | 16 | 2 | 16 | G | 1
| N2O [g/GJ_i] | 4 | 3 | 2 | 1 | 1 | 4 | 1 | 4 | G | 1
| Particles [g/GJ_i] | 2 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | G | 1
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.9 | 0.88 | 0.83 | 0.75 | 0.76 | 1.08 | 0.62 | 1.09 | [F, K]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.44 | 0.43 | 0.4 | 0.37 | 0.37 | 0.55 | 0.3 | 0.55 | [F, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.46 | 0.45 | 0.43 | 0.39 | 0.39 | 0.53 | 0.32 | 0.54 | [F, K]
| Variable O&M (*total) [2015-EUR/MWh_h] | 1.99 | 2.11 | 2.78 | 3.12 | 1.92 | 2.59 | 2.86 | 3.84 | [F, L]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 1.32 | 1.45 | 2.12 | 2.45 | 1.43 | 1.71 | 2.42 | 2.9 | [F, L]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 0.67 | 0.67 | 0.67 | 0.67 | 0.49 | 0.88 | 0.43 | 0.94 | [F, L]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 52300 | 50800 | 47900 | 42900 | 43400 | 59600 | 32800 | 55700 | F
Technology-specific data
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.93 | 0.9 | 0.86 | 0.78 | 0.79 | 1.12 | 0.64 | 1.12 | [I, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.45 | 0.44 | 0.42 | 0.38 | 0.38 | 0.57 | 0.31 | 0.57 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.48 | 0.46 | 0.44 | 0.4 | 0.41 | 0.55 | 0.33 | 0.55 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 2.05 | 2.18 | 2.87 | 3.22 | 1.99 | 2.3 | 2.96 | 3.42 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 54000 | 52400 | 49400 | 44200 | 44800 | 61600 | 33900 | 57500
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.08 | 0.08 | 0.07 | 0.07 | 0.07 | 0.09 | 0.06 | 0.09 | K
| Output of recovered condensate [t/MWh_i] | 0.09 | 0.09 | 0.09 | 0.09 | 0 | 0.09 | 0 | 0.09 | [D, L]
| Flue gas condensation | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, M]
| Combustion air humidification | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | [D, M]
| Additional heat potential with heat pumps (of thermal input) [] | 1.767% | 1.767% | 1.767% | 1.767% | 1% | 15% | 1% | 15% | D | 1
Notes:
A. The plant is directly producing hot water for District Heating by burning fuel on a grate.
B. Boilers up to 20 MW fuel input for hot water production are more or less standardized products with a high degree of fuel flexibility (type of biomass, humidity etc.)
C. The stated total efficiency does NOT consider auxiliary electricity consumption. It describes the total net amount of heat produced at the plant. This is contrary to CHP where the auxiliary electricity is subtracted from the production to yield the net electricity efficiency.
D. Since straw is relatively dry there is often only a minor efficiency advantage in using flue gas condensation. There is though an environmental advantage in having a scrubber in the flue gas stream. Direct condensation and combustion air humidification are included in all cases except in lower/upper range of 2020 and 2050. The system is optimised at DH return temperature 40°C and flow 80°C.
E. Load control of the heat production is important and units of this size can make rapid load variations. Similarly, the minimum load is quite low
F. Reference to heat output because of the lack of electricity production
G. Emissions shall comply with the order of the Danish EPA no 1535 of 2019 (Bekendtgørelse om miljøkrav for mellemstore fyringsanlæg), implementing the Medium Combustion Directive, Directive (EU) 2015/2193 of the European Parliament and of the Council of 25 November 2015 on the limitation of emissions of certain pollutants into the air from medium combustion plants.. It is anticipated that for the smaller units the supplier has an SNCR solution to reduce NOx emissions sufficiently. However, to reach NOx-levels below 40 g/GJ SCR is assumed. Warm start is starting with a glowing fuel layer on the grate.
I. The nominal investment is in the range 0.6 to 1.1 MEUR/MWth
J. Result of model calculation, there are reports of DH plants operating at lower power consumption
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and heat supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues, small share of staff-cost and maintenance cost. Electricity consumption is included for DH and associated costlisted separately, in addition. Cost for disposal of recovered flue gas condensate is included at a rate of 1.0 EUR/tonne of condensate. Revenues from sale of heat are not included. Taxes are not included. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.

## 09a Wood Chips extract. plant
Technology |  | Biomass CHP - extraction - wood chips - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 257.7 | 258.2 | 259.7 | 248.6 | 238.8 | 258.6 | 242.6 | 261.3 | A
| Electrical efficiency (net, annual average) [] | 40.8% | 40.9% | 41% | 39.4% | 37.8% | 41% | 38.5% | 41.4% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 43% | 43% | 43.2% | 41.4% | 39.8% | 43.1% | 40.4% | 43.6% | [A, H] | 1
| Cb coefficient (50°C/100°C) | 0.44 | 0.45 | 0.42 | 0.4 | 0.42 | 0.41 | 0.43 | 0.44
| Cv coefficient (50°C/100°C) | 0.14 | 0.14 | 0.14 | 0.13 | 0.13 | 0.13 | 0.13 | 0.14
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 1
| Space requirement [1000 m2/MW_e] | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 |  | 1
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 45% | 45% | 45% | 45% | 45% | 45% | 45% | 45%
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [E, G] | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 1
Environment
| SO2 (degree of desulphuring) [] | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | F | [1, 2, 3]
| NOX [g/GJ_i] | 30 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | F | [1, 2, 3]
| CH4 [g/GJ_i] | 3 | 2 | 2 | 1 | 1 | 3 | 0 | 3 | F | [1, 2, 3]
| N2O [g/GJ_i] | 10 | 8 | 6 | 5 | 5 | 10 | 3 | 10 | F | [1, 2, 3]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 | F | [1, 2, 3]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 2.6 | 2.5 | 2.4 | 2.3 | 2.4 | 3.1 | 2.2 | 3.3 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 1.6 | 1.6 | 1.5 | 1.4 | 1.5 | 1.9 | 1.4 | 2.1 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 1 | 0.9 | 0.9 | 0.8 | 0.8 | 1.1 | 0.8 | 1.2 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 2.6 | 2.6 | 2.6 | 2.7 | 2.8 | 2.6 | 2.7 | 2.5 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 70000 | 69000 | 64000 | 62000 | 66000 | 80000 | 57000 | 79000
Technology-specific data
| Nominal investment (*total) [2015-MEUR/MW_i] | 1.1 | 1.08 | 1.02 | 0.94 | 0.94 | 1.32 | 0.88 | 1.44 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.69 | 0.67 | 0.63 | 0.59 | 0.59 | 0.84 | 0.55 | 0.92 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.42 | 0.41 | 0.4 | 0.36 | 0.35 | 0.48 | 0.33 | 0.52 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | 1.11 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 30200 | 29500 | 27900 | 25500 | 26400 | 34400 | 23200 | 34200
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | K
Steam reheat | bar: ctrl to note
Flue gas condensation | bar: ctrl to note
| Combustion air humidification | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | M
| Additional heat potential with heat pumps (of thermal input) [] | 4.1% | 4.1% | 4.1% | 4.1% | 4.1% | 4.1% | 4.1% | 4.1% | C | 1
Notes:
A. The boiler in the plant is a circulating fluid bed boiler (CFB) producing steam to be used in a subsequent extraction steam turbine with steam re-heat.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield 22% (of thermal input) when operated with combustion air humidification and assuming 50 °C DH return temperature. DH water may be heated in two (or more) stages, first stage being direct condensation (at hardly any drop in electricity output), second stage extraction steam with drop in electricity output, cf. the Cv-value.
D. Secondary regulation normally relates to power production.
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator). Warm start-up time is particularly low for fluid bed types of plants.
F. It is to be expected that the NOx level is low from the CFB, and that the necessary DeNOx can be accomplished using SNCR, except where anticipated emission levels are below 20 g/GJ, in which case SCR is used. From 2017 NOx (and other emissions) must fulfil the BAT_AEL values of the LCP BREF note.
G. Warm start is starting with a glowing bed and a warm deaerator.
H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, facilities for chipping of logs, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities and energy supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949
3. Estimated from emission factors of 2006: 81 g/GJ NOx, 1.9 g/GJ for SO2, <1 g/GJ for CH4, 0.8 g/GJ for N2O, 10 g/GJ for Particles; cf. Nielsen, M., Nielsen, O.-K. & Thomsen, M. 2010: Emissions from decentralised CHP plants 2007 - Energinet.dk Environmental project no. 07/1882. Project report 5 - Emission factors and emission inventory for decentralised CHP production. National Environmental Research Institute, Aarhus University. 113 pp. - NERI Technical report No. 786. http://www.dmu.dk/Pub/FR786.pdf.

## 09b Wood Pellets extract. plant
Technology |  | Biomass CHP - extraction - wood pellets - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 356.4 | 357.6 | 358.7 | 358.4 | 347.3 | 359.4 | 351.7 | 364.4 | A
| Electrical efficiency (net, annual average) [] | 42.3% | 42.5% | 42.6% | 42.6% | 41.2% | 42.7% | 41.8% | 43.3% | [A, H] | 1
| Electrical efficiency (net, name plate) [] | 44.5% | 44.7% | 44.8% | 44.8% | 43.4% | 44.9% | 44% | 45.5% | [A, H] | 1
| Cb coefficient (50°C/100°C) | 0.59 | 0.59 | 0.59 | 0.52 | 0.57 | 0.52 | 0.59 | 0.53
| Cv coefficient (50°C/100°C) | 0.17 | 0.17 | 0.17 | 0.15 | 0.17 | 0.15 | 0.17 | 0.15 | I
Forced outage [] | bar: ctrl to upper
| Planned outage [weeks per year] | 3 | 3 | 3 | 3 | 2.6 | 3.5 | 2.3 | 3.8
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 1
| Construction time [years] | 5 | 5 | 5 | 5 | 5 | 1 | 1 | 1 |  | 1
| Space requirement [1000 m2/MW_e] | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: ctrl to upper
| Secondary regulation (of full load, per minute) [] | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | D | 1
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% |  | 1
| Warm start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | G | 1
| Cold start-up time [hours] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | E | 1
Environment
| SO2 (degree of desulphuring) [] | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% | 97.5% |  | [1, 2]
| NOX [g/GJ_i] | 20 | 20 | 20 | 10 | 10 | 30 | 10 | 20 | [C, F] | [1, 2]
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | [1, 2]
| N2O [g/GJ_i] | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 |  | [1, 2]
| Particles [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 2 | 0.1 | 1 |  | [1, 2]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 2.22 | 2.15 | 2.04 | 1.9 | 1.93 | 2.59 | 1.8 | 2.78 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_e] | 1.34 | 1.3 | 1.23 | 1.16 | 1.16 | 1.58 | 1.08 | 1.7 | K
| Nominal investment (installation) [2015-MEUR/MW_e] | 0.88 | 0.86 | 0.81 | 0.74 | 0.77 | 1 | 0.71 | 1.08 | K
| Variable O&M (*total) [2015-EUR/MWh_e] | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.1 | 1.2 | 1.1 | L
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 57000 | 55000 | 52000 | 49000 | 51000 | 63000 | 46000 | 63000
Technology-specific data
| Nominal investment (*total) [2015-MEUR/MW_i] | 0.99 | 0.96 | 0.92 | 0.85 | 0.84 | 1.16 | 0.79 | 1.26 | [J, K] | 1
| Nominal investment (equipment) [2015-MEUR/MW_i] | 0.59 | 0.58 | 0.55 | 0.52 | 0.51 | 0.71 | 0.48 | 0.77 | K
| Nominal investment (installation) [2015-MEUR/MW_i] | 0.39 | 0.38 | 0.36 | 0.33 | 0.33 | 0.45 | 0.31 | 0.49 | K
| Variable O&M (*total) [2015-EUR/MWh_i] | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | L
| Fixed O&M (*total) [2015-EUR/MW_i/y] | 25200 | 24600 | 23500 | 21900 | 22200 | 28300 | 20000 | 28600
| Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | K
Steam reheat | bar: ctrl to note
| Flue gas condensation | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | M
| Combustion air humidification | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | M
| Additional heat potential with heat pumps (of thermal input) [] | ctrl: 3.6%; upper: 3.6%; upper: 3.6%; note: C; ref: 1
Notes:
A. The boiler in the plant is a suspension fired boiler producing steam to be used in a subsequent extraction steam turbine with steam reheat.
C. Additional heat potential for heat pump is the flue gas condensation potential remaining after the direct condensation stage (condensation by heat exchange with DH-water). This comes in addition to direct condensation that may yield additional 6% (of thermal input) when operated with combustion air humidification and assuming 50 °C DH return temperature. DH water may be heated in two (or more) stages, first stage being direct condensation (at hardly any drop in electricity output), second stage extraction steam with drop in electricity output, cf. the listed Cv-value. For the 2050 estimate flue gas condensation has been included to super-optimize and show the order of advantage is a reduction of the Cv of 0.02 as resulting average for maximum heat output including condensation.
D. This is given by grid code (Energinet.dk)
E. A limiting factor for the hot and cold start-up times is the size of the hot water tank (deaerator).
F. This plant is equipped with a Tail-end SCR catalyst for DeNOx and an electrostatic precipitator for catching dust/fly ash
G. Warm start is starting with the steam system being pressurized.
H. The electricity efficiency is applicable for "name plate" and "annual average", respectively. The "annual average" electricity efficiency is lower than "name plate" due to due to the effects of load variations, turbine outages and other incidents. Efficiencies refer to thermal input by lower heating value. The parasitic electricity consumption has been subtracted in the listed electricity efficiencies.
I. The Cv value may vary according to the optimisation of the plant. A modest value representing a choice with current power/heat prices is shown.
J. Investment applies to a standard plant. There could be cost related to the actual project or site that adds to the total investment, e.g. additional fuel storage, conditions for foundation and harbour facilities. Financial data and Technological specific data are essentially the total cost either divided by the electric net capacity, i.e. corresponding to the indicated name plate efficiencies, or by the thermal input. This is to indicate that new plants may not fully take advantage of the technical capabilities for full electricity production capacity. The two cost for electricity and thermal input, respectively, are not to be added up!
K. Note that investments include only two days fuel storage, and more may be optimal, depending on fuel supply opportunities energy supply obligations, amongst other things. The additional investment is listed in the bottom row.
L. Variable O&M cost includes consumables (for FGT etc.), disposal of residues and maintenance cost. Cost for disposal of recovered flue gas condensate, if applicable, is not included. Electricity consumption is not included as a cost for CHP, and revenues from sale of electricity and heat are not included. Taxes are not included.
M. Binary value where 1 = yes and 0 = no
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Rambøll Danmark, internal evaluation based on either existing projects, supplier offers, or pre-project studies.
2. EU-commission, LCP BREF note. Thierry Lecomte, José Félix Ferrería de la Fuente, Frederik Neuwahl, Michele Canova, Antoine Pinasseau, Ivan Jankov, Thomas Brinkmann, Serge Roudier, Luis Delgado Sancho; Best Available Techniques (BAT) Reference Document for Large Combustion Plants; EUR 28836 EN; doi:10.2760/949

## 10 Stirling
Technology |  | Stirling engine - back pressure - biomass - medium
year |  | 2015 | 2020 | 2030 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 0.04 | 0.04 |  |  |  | 1
| Electrical efficiency (net, name plate) [] | 20% | 22% |  |  | A | 1
| Forced outage [] | 4% | 3% |  |  |  | 1
| Planned outage [weeks per year] | 3 | 2 |  |  |  | 1
| Technical lifetime [years] | 15 | 15 |  |  |  | 1
| Construction time [years] | 0.4 | 0.3 |  |  | B | 1
Regulation ability
| Cold start-up time [hours] | 1 | 1 |  |  |  | 1
Environment
| SO2 (degree of desulphuring) [] | 0% | 0% |  |  |  | 1
| NOX [ppm] | 130 | 100 |  |  |  | 1
| CH4 [ppm] | 0 | 0 |  |  |  | 1
| N2O [ppm] | 0 | 0 |  |  |  | 1
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 5 | 3.8 |  |  | [C, E] | 1
| Variable O&M (*total) [2015-EUR/MWh_e] | 26 | 21 |  |  | [D, E] | 1
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 32000 | 32000 |  |  | [D, E] | 1
Technology-specific data
| Generating capacity for one unit [MW_h] | 0.12 | 0.12 |  |  |  | 1
Notes:
A. The efficiency of the gasifier is 97%, while the total efficiency for the whole system is 90% (2020).
B. The plants may be delivered as pre-assembled container solutions reducing construction times on site to a couple of weeks.
C. Complete plant, including gasifier, combustion chambers, engines, control system, piping, and instrumentation.
D. O&M for the Stirling engine itself is (2010) around 16 EUR/MWh, while the remianing O&M costs are for biomass feeding, gasification, heat exchangers etc.
E. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Stirling DK, December 2009

## 11 SOFC-CHP
Technology |  | Solid oxide fuel cell - back pressure - biogas - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 0.25 | 2.5 | 10 | 20 |  |  |  |  | A | [3, *, *, *]
| Electrical efficiency (net, annual average) [] | 56% | 58% | 60% | 60% | 52% | 60% | 56% | 62% | B | [3, *, *, *]
| Electrical efficiency (net, name plate) [] | ctrl: 56%; ctrl: 58%; ctrl: 60%; ctrl: 60%
| Cb coefficient (50°C/100°C) | ctrl: 1.67; ctrl: 1.61; ctrl: 1.61; note: [C, L]; ref: [, *, *, *]
Cv coefficient (50°C/100°C)
Forced outage []
Planned outage [weeks per year]
| Technical lifetime [years] | 15 | 20 | 20 | 20 |  |  |  |  | D | [6, 6, *, *]
Construction time [years] | bar: ctrl to ctrl
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
| Minimum load (of full load) [] | ctrl: 70%; ctrl: 70%; ctrl: 70%; ctrl: 70%
| Warm start-up time [hours] | ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; note: E
| Cold start-up time [hours] | 25 | 25 | 25 | 25 |  |  |  |  | E | [*, *, *, *]
Environment
| SO2 (degree of desulphuring) [] | ctrl: 100%; ctrl: 100%; ctrl: 100%; ctrl: 100%; ref: 3
| NOX [g/GJ_i] | ctrl: 1.3; ctrl: 1.4; ctrl: 1.5; ctrl: 1.6; ref: 3
| CH4 [g/GJ_i] | 1.25 | 1.25 | 1.25 | 1.25 |  |  |  |  | F | 7
N2O [g/GJ_i] | bar: note to ref
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 8.3 | 3.3 | 2 | 0.8 | 2.7 | 5.8 | 0.4 | 1.3 | [G, H, I, J] | [8, 13]
| Nominal investment (equipment) [2015-MEUR/MW_e] | ctrl: 6.64; ctrl: 2.31; ctrl: 1.2; ctrl: 0.46; note: G
| Nominal investment (installation) [2015-MEUR/MW_e] | ctrl: 1.66; ctrl: 0.99; ctrl: 0.8; ctrl: 0.34; note: G
Variable O&M (*total) [2015-EUR/MWh_e]
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 415000 | 165000 | 100000 | 40000 | 135000 | 290000 | 20000 | 65000 | K | 8
Startup cost [2015-EUR/MW_e/startup]
Notes:
A. Installed systems consist of modules of app. 200 kWel power, these modules can be clustered into larger units. Today, often up to app. 2 MWel power and upwards. [5,8]
B. The electrical efficiency (based on the lower heating value, LHV) of Bloom Energy's systems decreases from an initial value of 60 % to 52 % by the end-of life for the stacks. This gives an average electrical efficiency of 56 % for the life-time of a stack. Uncertainties represent the aforementioned interval.
C. No CHP-systems in this power range are available, therefore, Bloom Energy ES-5710 unit has been chosen as the reference system. This system is a power producing system and does not take the produced heat into account. . The produced heat can be used as thermal storage, hot water production, heating or for feed in to the distributed heating system. High total efficiencies can be expected as the systems are compact and with a small surface area, leading to low heat losses and thereby high total system efficiency. Thus it is not unrealistic to assume a total efficiency above 90 % (thermal efficiency > 35 %) for this type of system.
D. Values correspond to the durability for the whole plant; the stack may be exchanged several times during the life time of the plant.
E. Start up from outdoor temperature or room temperature takes rather long time, this is mainly due to the large amount of ceramic material which require slow heating ramps. If the system is at operating temperature the stack can be started up quickly, assuming that gases are supplied and help systems are active. Also shut down can be performed quickly, not counting in the time required to cool the system.
F. Value for SOFC microCHP systems used here, since SOFC-CHP's has the same operating principle.
G. A bloom unit costs approximately 6600 euro per kWel. To this must the installation costs be added, which of course depends on the location and the size of the unit. Additional costs are also to cover for necessary modifications of the system, e.g. implementation of hot water storage and subsystems for exporting the heat from the unit to surrounding buildings or distributed heating grid.
H. Start up from outdoor temperature or room temperature takes rather long time, this is mainly due to the large amount of ceramic material which require slow heating ramps. If the system is at operating temperature the stack can be started up quickly, assuming that gases are supplied and help systems are active. Also shut down can be performed quickly, not counting in the time required to cool the system.
I. The best estimates for nominal investments in 2020, 2030 and 2050 are estimated from [9]. In 2020 an annual production of 50 units is assumed, in 2030 a yearly production of 250 units is assumed, and in 2050 a production of 4000 units per year is assumed.
J. Estimation of uncertainties for investment costs are estimated from [9] with an annual production of 10/150 units in 2020 and 1000/10000 units in 2050
K. Fixed O&M costs are estimated as 5% of the investment cost.
L. The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.
M. An asterisk (*) in the reference indicate high uncertainty or "guesstimate", where more certain data where not available
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. BloomEnergy, www.bloomenergy.com, 2014-11-11
2. https://www.mhps.com/en/technology/index.html, 2014-11-14
3. BloomEnergy, Product datasheet: ES-5710 Energy Saver, November 2014: http://c0688662.cdn.cloudfiles.rackspacecloud.com/downloads_pdf_Bloomenergy_DataSheet_ES-5710.pdf
4. BloomEnergy, Product datasheet: ES-5700 Energy Saver, November 2014: http://c0688662.cdn.cloudfiles.rackspacecloud.com/downloads_pdf_Bloomenergy_DataSheet_ES-5700.pdf
5. Iskov H., Rasmussen N.B., "Update of technology data for energy plants: Fuel cells, electrolysis and technologies for bio-SNG", Danish gas Technology centre, 2013.
6. Fuel Cell and Hydrogen Joint Undertaking: "Multi - Annual Work Plan 2014-2020", adopted 2014-06-30
7. http://www.asue.de, 2014-11-17
8. BloomEnergy Server, http://en.wikipedia.org/wiki/Bloom_Energy_Server, 2015-02-02
13. Chick, LA; Gotthold, DW; Weimar, MR; Whyatt, GA, Cost Study for Manufacturing of Solid Oxide Fuel Cell Power Systems, 2013, Pacific Northwest National Laboratory prepared for the U.S. Department of Energy.

## 12 LT-PEMFC CHP
Technology |  | Low temp PEM fuel cell - back pressure - hydrogen - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 0.05; ctrl: 0.1; ctrl: 1; ctrl: 2; ref: 5
| Electrical efficiency (net, annual average) [] | 45% | 50% | 50% | 50% | 45% | 52% | 46% | 53% | A | [3, 5]
| Electrical efficiency (net, name plate) [] | ctrl: 45%; ctrl: 50%; ctrl: 50%; ctrl: 50%; ref: 5
| Cb coefficient (50°C/100°C) | ctrl: 1.25; ctrl: 1.25; ctrl: 1.25; note: D
Cv coefficient (50°C/100°C)
| Forced outage [] | ctrl: 0.1%; ctrl: 0.1%; ctrl: 0.1%; ctrl: 0.1%
| Planned outage [weeks per year] | ctrl: 0.1; ctrl: 0.1; ctrl: 0.1
| Technical lifetime [years] | ctrl: 10; ctrl: 10; ctrl: 10; ctrl: 10; ref: 5
Construction time [years] | bar: ctrl to ctrl
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | ctrl: 50%; ctrl: 25%; ctrl: 2.5%; ctrl: 1.25%
Secondary regulation (of full load, per minute) []
| Minimum load (of full load) [] | ctrl: 10%; ctrl: 10%; ctrl: 10%; ctrl: 10%
| Warm start-up time [hours] | ctrl: 0.01; ctrl: 0.01; ctrl: 0.01; ctrl: 0.01
Cold start-up time [hours]
Environment
| SO2 (degree of desulphuring) [] | ctrl: 100%; ctrl: 100%; ctrl: 100%; ctrl: 100%
| NOX [g/GJ_i] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| CH4 [g/GJ_i] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| N2O [g/GJ_i] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 1.9 | 1.3 | 1.1 | 0.8 | 1.1 | 1.6 | 0.5 | 0.9 | B | [3, 4]
| Nominal investment (equipment) [2015-MEUR/MW_e] | ctrl: 1.6; ctrl: 1; ctrl: 0.8; ctrl: 0.6; ref: 4
| Nominal investment (installation) [2015-MEUR/MW_e] | ctrl: 0.3; ctrl: 0.3; ctrl: 0.3; ctrl: 0.2; ref: 4
Variable O&M (*total) [2015-EUR/MWh_e]
| Fixed O&M (*total) [2015-EUR/MW_e/y] | ctrl: 95000; ctrl: 65000; ctrl: 55000; ctrl: 40000; note: C
Technology-specific data
| Minimum load efficiency [] | ctrl: 30%; ctrl: 35%; ctrl: 35%; ctrl: 35%; ref: 5
Notes:
A. Uncertainties for efficiency based on [2]
B. Estimation of uncertainties for nominal investment costs based on [2]
C. Fixed O&M costs are estimated to 5% of the investment cost based on [2]
D. The heat efficiency, which can be derived, depends on the return temperature of the cooling circuit and the size of the heat exchanger.
E. An asterisk (*) in the reference indicate high uncertainty or "guesstimate", where more certain data where not available.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. International Energy Agency, 2015, Technology Roadmap - Hydrogen and Fuel Cells.
4. Ea Energy Analyses et al. 2016, Technology Data for Hydrogen Technologies.
5. Practical data and expert opinion from Dantherm Power

## 20 Onshore turbines
Technology |  | Onshore wind turbine, utility - renewable power - wind - large
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 3.1 | 4.2 | 5 | 5.5 | 6 | 2 | 6 | 1.5 | 8 | A1 | 3
| Forced outage [] | 3% | 2.5% | 2% | 1.8% | 1.5% | 1% | 5% | 1% | 5% | B | 4
| Planned outage [weeks per year] | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 | C | 4
| Technical lifetime [years] | 25 | 27 | 30 | 30 | 30 | 25 | 35 | 25 | 40 | D | 14
| Construction time [years] | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 3 | 1 | 3 | E | 4
Space requirement [1000 m2/MW_e] | bar: note
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 1.33 | 1.12 | 1.04 | 0.98 | 0.96 | 0.77 | 1.16 | 0.8 | 1.19 |  | [16, 2, 4]
| Nominal investment (equipment) [2015-MEUR/MW_e] | 0.89 | 0.71 | 0.64 | 0.59 | 0.58 | 0.57 | 0.86 | 0.46 | 0.69 |  | 25
| Nominal investment (installation) [2015-MEUR/MW_e] | 0.12 | 0.09 | 0.08 | 0.08 | 0.07 | 0.07 | 0.11 | 0.06 | 0.09 | M | 25
| Nominal investment (decommissioning of existing turbines) [2015-MEUR/MW_e] | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.04 | 0.03 | 0.04 |  | 25
| Nominal investment (grid connection) [2015-MEUR/MW_e] | 0.06 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.06 | 0.04 | 0.06 |  | 25
| Nominal investment (other, i.e. compensation of neighbours) [2015-MEUR/MW_e] | 0.13 | 0.14 | 0.14 | 0.14 | 0.14 | 0.11 | 0.17 | 0.11 | 0.17 | I | [25, 26]
| Nominal investment (land rent) [2015-MEUR/MW_e] | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.07 | 0.1 | 0.07 | 0.1 |  | 25
| Variable O&M (*total) [2015-EUR/MWh_e] | 2.8 | 1.5 | 1.35 | 1.24 | 1.22 | 1.2 | 1.8 | 0.97 | 1.46
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 25600 | 14000 | 12600 | 11592 | 11340 | 11200 | 16800 | 9072 | 13608 | I | [25, 26]
Technology-specific data
| Availability [] | 96.7% | 97.2% | 97.7% | 97.7% | 98.2% | 98.9% | 94.5% | 98.9% | 94.5%
| Hub height [m] | 85 | 85 | 100 | 105 | 110 | 85 | 120 | 85 | 150 |  | [4, 26]
| Rotor diameter [m] | 106 | 130 | 145 | 155 | 165 | 90 | 130 | 100 | 150 | K | [4, 26]
| Specific power [W_e/m2] | 351.29 | 316.43 | 302.79 | 291.48 | 280.6 | 314.38 | 452.04 | 190.99 | 452.71
| Average capacity factor [] | 35.39% | 38.81% | 41.1% | 42.24% | 43.38% | 22.83% | 45.66% | 22.83% | 51.37% |  | [4, 26]
| Average annual full-load hours [MWh_e/MW_e] | 3100 | 3400 | 3600 | 3700 | 3800 | 2000 | 4000 | 2000 | 4500 | [A, L] | 3
Notes:
A1. The capacity is set to 3.5 MW in 2015 and 2020 based on data of current wind turbines and under the anticipation that the maximum height will not exeed 150m before 2020. From 2030 a slight increase in generator size, and hub height is assumed, where the effect of expected removal of present max. 150m tip height.
A. The full load hours (annual produktion (MWh) per installed power (MW)) depending on the actual location of the wind farm, wake losses and technological characteristics of the individual turbine. The value is an average for the expected locations of the wind farms. FLH also depends on wake losses, noise reduction and technological characteristics of the individual turbine. The level for 2020 is based on expectations from the November 18 auction winners locations and the 2019 prefered technology choice. For 2030 and 2050 a slight increase is assumed based on decrease in specific power and increase in hub height.
B. Modern turbines has typically higher forced outage than older smaller turbines had when they were newer due to more complex technology.
C. Planned outage is typically 1-2 service visits a year, with a maximum duration of one work day, but there can also be planned outage due to shadow flicker stop or sector management (protect turbines at given wind speeds and directions, where they are dense spaced).
D. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
E. The construction time is the periode from FID to commissioning. But from first "dig" to turbines are in operation less than ½ a year is needed for smaller wind farms (clusters), where the similar periode for larger wind farms will be longer. The planning time from idea to construction starts will typically be 2-3 years, but can be essentially more if permitting problems occour.
F. An area of around 50 m x 50 m is needed for a modern wind turbine. Another way of defining the "area use" could be the noise zone, which ranges up to 600-800 m from the wind turbine in worst case.
G. Wind turbines can be downward regulated within very short time and can therefore (if the wind is blowing) be used in both the primary and secondary downward regulation.
H. 2015 Investment costs are based on a number of prospects for projects published in relation to Køberetsordningen. 2020 investment costs are based on updated data from Køberetsordningen. Note that the investment costs listed here includes construction loan interests
I. 75 % of the total yearly O&M costs are assumed to be fixed cost and 25 % are assumed to be variable cost.
K. Currently only turbines up to 150 m total height is installed commercially in Denmark because of strict demands to higher turbines. No change in the national regulation is assumed until after 2020. Some test sites allow for larger turbines. Aboard e.g. in Germany turbines with at total higher of 200 m is installed today.
L. It is expected that the production (FLH) increase 13% from 2015 to 2020 and 3% from 2020-2030 and 1% per decade from 2030-2050
M. Includes development cost.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
2. DTU International Energy Report - Wind Energy, DTU, 2014
3. Master data register of wind turbines at end of December 2014, Danish Energy Agency, 2015
4. Nielsen, P. et. al., Vindmøllers økonomi EUDP projekt 33033-0196, 2010
14. Information from Energinet.dk based on analyses of installed projects (2013-14), published under "Købsretsordningen", 2015
15. Når all-inclusive service alligevel ikke dækker alt, Naturlig Energi, nov. 2014
16. Schwabe, P., Lensink, S. & Hand, M., IEA Wind Task 26: Multi-national case study of the financial cost of wind energy, 2011
18. Hvor længe holder en mølle, Naturlig Energi, januar 2012
25. Analysis of "køberets" projects 2017-18
26. Interviews with project developers and suppliers dec.18-jan.19

## 20 Domestic turbines
Technology |  | Onshore wind turbine, residential - renewable power - wind - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0.03 | 0 | 0.03
| Forced outage [] | 3% | 3% | 3% | 3% | 2% | 10% | 2% | 10%
| Planned outage [weeks per year] | 0.16 | 0.16 | 0.16 | 0.16 | 0.05 | 0.26 | 0.05 | 0.26 | B
| Technical lifetime [years] | ctrl: 20; ctrl: 20; ctrl: 20; ctrl: 20
| Construction time [years] | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5
| Space requirement [1000 m2/MW_e] | ctrl: 0.8; ctrl: 0.8; ctrl: 0.8; ctrl: 0.8; note: C
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 4 | 3.8 | 3.61 | 3.43 | 3 | 6 | 3 | 6 | [E, F]
| Nominal investment (equipment) [2015-MEUR/MW_e] | 0.9 | 0.9 | 0.9 | 0.9 | 0.85 | 0.95 | 0.85 | 0.95 | [E, F]
| Nominal investment (installation) [2015-MEUR/MW_e] | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.05 | 0.15 | 0.05 | [E, F]
Variable O&M (*total) [2015-EUR/MWh_e]
| Fixed O&M (*total) [2015-EUR/MW_e/y] | ctrl: 100000; ctrl: 95000; ctrl: 90000; ctrl: 85000; note: G
Technology-specific data
| Fixed O&M (*total) [2015-EUR/unit/y] | 540 | 540 | 540 | 540 | 350 | 700 | 350 | 700 | [E, F]
| Hub height [m] | 18 | 18 | 18 | 18 | 14 | 18 | 14 | 18 | H
| Rotor diameter [m] | 8 | 11 | 12 | 14 | 4 | 14 | 4 | 14 | H
| Average annual full-load hours [MWh_e/MW_e] | 1600 | 1800 | 2000 | 2200 | 1000 | 2300 | 1000 | 2300 | [A, J]
Notes:
A. The annual production is very sensitive to conditions at the actual site. Values outside the range is observed.
B. The maintenance normally consists of 1 -2 annual service visits.
C. An area of around 5 m x 5 m is needed for at small wind turbine. The real "area use" is the noise zone, which ranges up to 100 m from the wind turbine in worst case.
D. Not considered relevant for small domestic turbines.
E. Based on information from manufacturers and resellers. The
F. The prices depends significantly on turbine size (5 kW - 6 MEUR/MW; 10 kW - 4 MEUR/MW ; 25 kW - 3 MEUR/MW)
G. The service cost is assumed fixed to 100EUR/kW/y.
H. Domestic turbines have a maximum total height of 25 m according to Danish regulations.
J. No development in the capacity factor is expected, because no changing in the size limitation (legislation) is expected. And because location is crucial and one must expect the turbines is put up at the best positions already. But change in legislation i
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
NA. NA

## 21 Offshore turbines
Technology |  | Offshore wind turbines - renewable power - wind - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 8.4 | 15 | 20 | 25 | 30 | 12.75 | 17.25 | 22.5 | 37.5 | A | 1, 2
| Forced outage [] | 1.909% | 1.759% | 1.75% | 1.732% | 1.714% | 1.759% | 1.759% | 1.714% | 1.714% | B
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | B
| Technical lifetime [years] | 27 | 30 | 30 | 30 | 30 | 25 | 35 | 25 | 35 | C
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 3 | 1.5 | 2.5 | D
| Space requirement [1000 m2/MW_e] | 165.36 | 177.36 | 171.96 | 169.84 | 171.26 | 150.76 | 203.96 | 128.44 | 214.07 | E | 3
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Minimum load (of full load) []
Warm start-up time [hours]
Cold start-up time [hours]
Financial data
| Nominal investment (*total) [2020-MEUR/MW_e] | 2.12 | 1.88 | 1.8 | 1.68 | 1.64 | 1.88 | 1.88 | 1.64 | 1.64 | F | 3
| Nominal investment (installation) [2020-MEUR/MW_e] | 0.54 | 0.4 | 0.37 | 0.33 | 0.32 | 0.4 | 0.4 | 0.32 | 0.32 |  | 3
| Nominal investment (project development etc.) [2020-MEUR/MW_e] | 0.38 | 0.31 | 0.28 | 0.25 | 0.23 | 0.26 | 0.36 | 0.17 | 0.34 |  | 3, 6
| Nominal investment (array cables) [2020-MEUR/MW_e] | 0.03 | 0.02 | 0.02 | 0.01 | 0.01 | 0.02 | 0.02 | 0.01 | 0.02 |  | 3
| Nominal investment (foundation) [2020-MEUR/MW_e] | 0.21 | 0.21 | 0.22 | 0.22 | 0.21 | 0.18 | 0.25 | 0.16 | 0.32 |  | 3, 4
| Nominal investment (grid connection) [2020-MEUR/MW_e] | 0.25 | 0.24 | 0.24 | 0.25 | 0.26 | 0.2 | 0.28 | 0.2 | 0.4 |  | 3, 5
| Nominal investment (turbines) [2020-MEUR/MW_e] | 0.72 | 0.69 | 0.67 | 0.61 | 0.61 | 0.59 | 0.8 | 0.46 | 0.91 |  | 3
| Variable O&M (*total) [2020-EUR/MWh_e] | 5 | 4.17 | 3.89 | 3.42 | 3.25 | 3.55 | 4.8 | 2.44 | 4.88 | H | 3
| Fixed O&M (*total) [2020-EUR/MW_e/y] | 50000 | 42000 | 39000 | 34000 | 33000 | 35700 | 48300 | 24750 | 49500 | H | 3
Technology-specific data
| Hub height [m] | 103.5 | 138 | 155 | 170 | 185 | 124.2 | 151.8 | 157.25 | 212.75 |  | 1
| Rotor diameter [m] | 167 | 236 | 270 | 300 | 330 | 212.4 | 259.6 | 280.5 | 379.5 |  | 1
| Specific power [W_e/m2] | 383.49 | 342.91 | 349.31 | 353.68 | 350.75 | 359.84 | 325.9 | 364.11 | 331.53 | I | 1
| Specific area coverage [MW_e/km2] | 6.05 | 5.64 | 5.82 | 5.89 | 5.84 | 6.63 | 4.9 | 7.79 | 4.67 | E | 3
| Average annual full-load hours [MWh_e/MW_e] | 4400 | 4775 | 4800 | 4850 | 4900 | 4300 | 5250 | 4050 | 5500 | J | 3
Notes:
A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
E. Calculated based on average spacing of 8 RD between turbines and a square layout. Horns Rev 3 has 9.5, but also quite low wake losses. With 2020 WTG size 8RD corresponds to 6 MW/km^2
F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
G. Other is planning & development, environmental impact assessment, insurances and finance costs.
H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Stiesdal, Offshore wind turbine size prediction tool.xlsx, with changes by Danish Energy Agency.
2. DTU Wind Energy: Pushing the physics of the large turbines of the future. 2021. Published in DTU International Energy Report 2021: Perspectives on Wind Energy. https://doi.org/10.11581/DTU.00000208
3. EMD cost and AEP Excel calculation tool
4. EA Energy Analyse/Cowi April 20 slide 25: https://www.ea-energianalyse.dk/wp-content/uploads/2020/05/1949_Offshore-wind-and-infrastructure.pdf
5. From ENS 2021: FT - omkostninger Anholt, HR3, KF.xlsx
6. Interview with Per Stenholt, Vattenfall, November 21

## 21 Near shore turbines
Technology |  | Offshore wind turbines, nearshore - renewable power - wind - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | 8.4 | 10 | 15 | 15 | 15 | 8.5 | 11.5 | 11.25 | 18.75 | A | 1, 2
| Forced outage [] | 2.048% | 1.942% | 1.887% | 1.887% | 1.887% | 1.942% | 1.942% | 1.887% | 1.887% | B
| Planned outage [weeks per year] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | B
| Technical lifetime [years] | 27 | 30 | 30 | 30 | 30 | 25 | 35 | 25 | 35 | C
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 2 | 3 | 1.5 | 2.5 | D
| Space requirement [1000 m2/MW_e] | 32.02 | 35.18 | 35.81 | 35.81 | 35.81 | 29.91 | 40.46 | 26.86 | 44.76 | E | 3
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Minimum load (of full load) []
Warm start-up time [hours]
Cold start-up time [hours]
Financial data
| Nominal investment (*total) [2020-MEUR/MW_e] | 1.7 | 1.49 | 1.38 | 1.24 | 1.19 | 1.49 | 1.49 | 1.19 | 1.19 | F | 3
| Nominal investment (installation) [2020-MEUR/MW_e] | 0.39 | 0.31 | 0.25 | 0.23 | 0.22 | 0.31 | 0.31 | 0.22 | 0.22 |  | 3
| Nominal investment (project development etc.) [2020-MEUR/MW_e] | 0.39 | 0.33 | 0.29 | 0.26 | 0.25 | 0.28 | 1.31 | 0.18 | 0.98 |  | 3, 6
| Nominal investment (array cables) [2020-MEUR/MW_e] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.05 | 0.01 | 0.04 |  | 3
| Nominal investment (foundation) [2020-MEUR/MW_e] | 0.13 | 0.13 | 0.12 | 0.11 | 0.11 | 0.11 | 0.51 | 0.08 | 0.42 |  | 3, 4
| Nominal investment (grid connection) [2020-MEUR/MW_e] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.2 | 0.04 | 0.19 |  | 3, 5
| Nominal investment (turbines) [2020-MEUR/MW_e] | 0.72 | 0.66 | 0.65 | 0.58 | 0.56 | 0.56 | 2.63 | 0.42 | 2.24 |  | 3
| Variable O&M (*total) [2020-EUR/MWh_e] | 5 | 4.17 | 3.89 | 3.42 | 3.25 | 3.55 | 16.69 | 2.44 | 13.01 | H | 3
| Fixed O&M (*total) [2020-EUR/MW_e/y] | 50000 | 42000 | 39000 | 34000 | 33000 | 35700 | 48300 | 24750 | 49500 | H | 3
Technology-specific data
| Hub height [m] | 103.5 | 115.5 | 138 | 138 | 138 | 98.17 | 132.82 | 103.5 | 207 |  | 1
| Rotor diameter [m] | 167 | 191 | 236 | 236 | 236 | 162.35 | 219.65 | 177 | 354 |  | 1
| Specific power [W_e/m2] | 383.49 | 349.01 | 342.91 | 342.91 | 342.91 | 410.61 | 303.49 | 457.21 | 190.5 | I | 1
| Specific area coverage [MW_e/km2] | 31.23 | 28.42 | 27.92 | 27.92 | 27.92 | 33.44 | 24.71 | 37.23 | 22.34 | E | 3
| Average annual full-load hours [MWh_e/MW_e] | 4100 | 4325 | 4450 | 4450 | 4450 | 3675 | 4975 | 3250 | 6500 | J | 3
Notes:
A1. General note: The data sheet focusses on Danish conditions and experience level and cannot be assumed general for offshore wind.
A. Starting point for 2020 is based on latest two DK projects, Horns Rev 3, 8.3MW (2018) and Kriegers Flak 8.4MW (2021). For future projects 15MW is already seen.
B. Offshore turbines have typically higher forced outage than onshore due to access problems in harsh weather. In total a loss of ca. 5% is expected, of which 2% is assumed grid losses and thereby 3% outage is converted to 1 week outage in total
C. The life time depends on the wind conditions; average annual speed and turbulence, relative to the design class of the turbine
D. The construction time is the period from FID to commissioning. The construction time depends on the size of the project, vessel availability and weather conditions.
E. For Nearshore the space requirements becomes "artificial", while typically 1-row projects will be expected. The space is here calculated based on square layout to give a number.
F. The cost includes cost of wind turbines, foundation, installation, planning & development and financing, internal and external grid (array cable, substation, and export cable).
G. Other is planning & development, environmental impact assessment, insurances and finance costs.
H. Roughly 70 % of the total yearly O&M costs are assumed to be fixed cost and 30 % are assumed to be variable cost depending on capacity factor. [A previous version listed this share wrongly as 80/20.]
I. The Specific power is assumed to increase slightly in time because of better wind resource due to larger hub heights
J. The full load hours are reduced with outage time mentioned under "Energy/technical data" according to the Technology Catalogue guideline. Full load hours are thus net full load hours after outages.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Stiesdal, Offshore wind turbine size prediction tool.xlsx, with changes by Danish Energy Agency.
2. DTU Wind Energy: Pushing the physics of the large turbines of the future. 2021. Published in DTU International Energy Report 2021: Perspectives on Wind Energy. https://doi.org/10.11581/DTU.00000208
3. EMD cost and AEP Excel calculation tool
4. EA Energy Analyse/Cowi April 20 slide 25: https://www.ea-energianalyse.dk/wp-content/uploads/2020/05/1949_Offshore-wind-and-infrastructure.pdf
5. From ENS 2021: FT - omkostninger Anholt, HR3, KF.xlsx
6. Interview with Per Stenholt, Vattenfall, November 21

## 22 Rooftop PV residential
Technology |  | PV - renewable power - solar - residential rooftop
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 0.006; ctrl: 0.006; ctrl: 0.006; ctrl: 0.006; ctrl: 0.006; note: B3,C
Forced outage [] | bar: ctrl to ctrl
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 30; ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Space requirement [1000 m2/MW_e] | ctrl: 6.36; ctrl: 5.12; ctrl: 4.57; ctrl: 4.29; ctrl: 4.04; ref: 6
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Financial data
| Nominal investment (*total) [2020-MEUR/MW_e] | 1.67 | 1.24 | 0.84 | 0.7 | 0.64 | 1.19 | 1.3 | 0.54 | 0.85 | M,O | 2, 4
| Nominal investment (*total, per DC) [2020-MEUR/MW_e] | 1.59 | 1.18 | 0.8 | 0.67 | 0.61 | 1.13 | 1.24 | 0.52 | 0.81 | M,N | 2, 4
| Nominal investment (grid connection) [2020-MEUR/MW_e] |  | 0.03 | 0.03 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02
| Nominal investment (inverter) [2020-MEUR/MW_e] |  | 0.22 | 0.14 | 0.12 | 0.1 | 0.21 | 0.23 | 0.09 | 0.12
| Nominal investment (pv modules) [2020-MEUR/MW_e] | 0.81 | 0.49 | 0.27 | 0.2 | 0.17 | 0.47 | 0.51 | 0.14 | 0.33 | M,O
| Nominal investment (installation) [2020-MEUR/MW_e] |  | 0.13 | 0.11 | 0.09 | 0.09 | 0.13 | 0.14 | 0.08 | 0.1
| Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | 0.86 | 0.21 | 0.17 | 0.15 | 0.14 | 0.2 | 0.22 | 0.13 | 0.16
Nominal investment (soft costs) [2020-MEUR/MW_e]
| Fixed O&M (*total) [2020-EUR/MW_e/y] | 16700 | 13400 | 10700 | 9600 | 8900 | 12100 | 14800 | 8100 | 9900 | P
Fixed O&M (land rent) [2020-EUR/MW_e/y]
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 0.0063; ctrl: 0.0063; ctrl: 0.0063; ctrl: 0.0063; ctrl: 0.0063; note: B3,C
| Space requirement (per DC) [1000m2/MW_e] | ctrl: 6.06; ctrl: 4.88; ctrl: 4.35; ctrl: 4.08; ctrl: 3.85; ref: 6
| Nominal investment (installation, per DC) [2020-MEUR/MW_e] |  | 0.27 | 0.22 | 0.19 | 0.18 | 0.26 | 0.28 | 0.16 | 0.2
| Nominal investment (inverter, per DC) [2020-MEUR/MW_e] |  | 0.21 | 0.14 | 0.11 | 0.1 | 0.2 | 0.22 | 0.08 | 0.12
| Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | 0.82 | 0.2 | 0.16 | 0.15 | 0.14 | 0.19 | 0.21 | 0.12 | 0.15
| Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | 0.78 | 0.47 | 0.26 | 0.19 | 0.17 | 0.45 | 0.49 | 0.13 | 0.31 | M,O
| Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] |  | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02
| Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | 15900 | 12800 | 10200 | 9100 | 8500 | 11500 | 14100 | 7700 | 9400 | P
Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y]
| Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | ctrl: 12800; ctrl: 10200; ctrl: 9100; ctrl: 8500
| Average annual degradation of full-load hours [] | ctrl: 0.5%; ctrl: 0.4%; ctrl: 0.3%; ctrl: 0.3%; ctrl: 0.3%
| Global horizontal irradiance [MWh/m2/y] | 1068 | 1068 | 1068 | 1068 | 1068 |  |  |  |  | A | 1
| Transposition factor | ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; note: E
| Performance ratio (contribution from bifaciality) [] | ref: 3
| Performance ratio (measure of combined losses) [] | ctrl: 79%; ctrl: 86%; ctrl: 95%; ctrl: 96%; ctrl: 97%; note: F
| PV module conversion efficiency [] | 16.5% | 20.5% | 23% | 24.5% | 26% |  |  |  |  | U | 3
| Inverter lifetime [years] | ctrl: 10; ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; ref: 6
| Sizing factor (DC/AC) [W_e/W_e] | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 |  |  |  |  | D | 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 934.72; ctrl: 1010.33; ctrl: 1116.06; ctrl: 1127.81; ctrl: 1139.56; note: A1,I
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 981.46; ctrl: 1060.84; ctrl: 1171.86; ctrl: 1184.2; ctrl: 1196.53; note: A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 22 Rooftop PV comm.&industrial
Technology |  | PV - renewable power - solar - commercial/industrial rooftop
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; note: B2,C
Forced outage [] | bar: ctrl to ctrl
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 30; ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Space requirement [1000 m2/MW_e] | ctrl: 6.67; ctrl: 5.37; ctrl: 4.78; ctrl: 4.49; ctrl: 4.23; ref: 6
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Financial data
| Nominal investment (*total) [2020-MEUR/MW_e] | 1.43 | 0.87 | 0.57 | 0.46 | 0.41 | 0.86 | 0.92 | 0.36 | 0.59 | M,O | 2, 4
| Nominal investment (*total, per DC) [2020-MEUR/MW_e] | 1.3 | 0.79 | 0.51 | 0.42 | 0.38 | 0.78 | 0.84 | 0.33 | 0.53 | M,N | 2, 4
| Nominal investment (grid connection) [2020-MEUR/MW_e] |  | 0.04 | 0.04 | 0.03 | 0.03 | 0.04 | 0.05 | 0.03 | 0.03
| Nominal investment (inverter) [2020-MEUR/MW_e] |  | 0.17 | 0.11 | 0.09 | 0.08 | 0.17 | 0.18 | 0.07 | 0.1
| Nominal investment (pv modules) [2020-MEUR/MW_e] | 0.81 | 0.44 | 0.24 | 0.18 | 0.15 | 0.43 | 0.46 | 0.12 | 0.29 | M,O
| Nominal investment (installation) [2020-MEUR/MW_e] |  | 0.13 | 0.11 | 0.09 | 0.09 | 0.13 | 0.14 | 0.08 | 0.1
| Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | 0.61 | 0.09 | 0.07 | 0.06 | 0.06 | 0.09 | 0.09 | 0.05 | 0.07
Nominal investment (soft costs) [2020-MEUR/MW_e]
| Fixed O&M (*total) [2020-EUR/MW_e/y] | 14300 | 10600 | 8900 | 8000 | 7500 | 9500 | 11700 | 6700 | 8300 | P
Fixed O&M (land rent) [2020-EUR/MW_e/y]
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 0.11; ctrl: 0.11; ctrl: 0.11; ctrl: 0.11; ctrl: 0.11; note: B2,C
| Space requirement (per DC) [1000m2/MW_e] | 6.06 | 4.88 | 4.35 | 4.08 | 3.85 |  |  |  |  | W | 6
| Nominal investment (installation, per DC) [2020-MEUR/MW_e] |  | 0.12 | 0.1 | 0.09 | 0.08 | 0.12 | 0.13 | 0.07 | 0.09
| Nominal investment (inverter, per DC) [2020-MEUR/MW_e] |  | 0.16 | 0.1 | 0.08 | 0.07 | 0.16 | 0.17 | 0.06 | 0.09
| Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | 0.56 | 0.08 | 0.06 | 0.06 | 0.05 | 0.08 | 0.08 | 0.05 | 0.06
| Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | 0.74 | 0.4 | 0.22 | 0.16 | 0.14 | 0.39 | 0.42 | 0.11 | 0.26 | M,O
| Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] |  | 0.04 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.02 | 0.03
| Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | 13000 | 9600 | 8100 | 7300 | 6800 | 8600 | 10600 | 6100 | 7500 | P
Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y]
| Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | ctrl: 13000; ctrl: 9600; ctrl: 8100; ctrl: 7300; ctrl: 6800
| Average annual degradation of full-load hours [] | ctrl: 0.5%; ctrl: 0.4%; ctrl: 0.3%; ctrl: 0.3%; ctrl: 0.3%
| Global horizontal irradiance [MWh/m2/y] | 1068 | 1068 | 1068 | 1068 | 1068 |  |  |  |  | A | 1
| Transposition factor | ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; ctrl: 1.1; note: E
| Performance ratio (contribution from bifaciality) [] | ctrl: 0%; ctrl: 0%; ctrl: 0%; ctrl: 1%; ctrl: 2%; ref: 3
| Performance ratio (measure of combined losses) [] | ctrl: 81%; ctrl: 86%; ctrl: 95%; ctrl: 96%; ctrl: 97%; note: F
| PV module conversion efficiency [] | 16.5% | 20.5% | 23% | 24.5% | 26% |  |  |  |  | U | 3
| Inverter lifetime [years] | ctrl: 10; ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; ref: 6
| Sizing factor (DC/AC) [W_e/W_e] | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 |  |  |  |  | D | 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 950.59; ctrl: 1010.33; ctrl: 1116.06; ctrl: 1127.81; ctrl: 1139.56; note: A1,I
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1045.65; ctrl: 1111.36; ctrl: 1227.67; ctrl: 1240.59; ctrl: 1253.51; note: A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 22 Utility-scale PV
Technology |  | PV - renewable power - solar - utility-scale, ground mounted
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 4; ctrl: 40; ctrl: 40; ctrl: 40; ctrl: 40
Forced outage [] | bar: ctrl to ctrl
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 30; ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5
| Space requirement [1000 m2/MW_e] | 20.25 | 13.75 | 12.26 | 11.51 | 10.84 |  |  |  |  | B,B1 | 6
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
Financial data
| Nominal investment (*total) [2020-MEUR/MW_e] | 1.55 | 0.56 | 0.38 | 0.32 | 0.29 | 0.54 | 0.6 | 0.25 | 0.4 | M,N,O,Q | 2, 4
| Nominal investment (*total, per DC) [2020-MEUR/MW_e] | 1.15 | 0.45 | 0.31 | 0.26 | 0.23 | 0.44 | 0.48 | 0.2 | 0.32 | M,N,O,Q | 2, 4
| Nominal investment (grid connection) [2020-MEUR/MW_e] | 0.09 | 0.06 | 0.05 | 0.04 | 0.04 | 0.06 | 0.07 | 0.04 | 0.05
| Nominal investment (inverter) [2020-MEUR/MW_e] | 0.11 | 0.03 | 0.02 | 0.02 | 0.01 | 0.03 | 0.03 | 0.01 | 0.02
| Nominal investment (pv modules) [2020-MEUR/MW_e] | 0.89 | 0.26 | 0.14 | 0.11 | 0.09 | 0.25 | 0.27 | 0.07 | 0.17
| Nominal investment (installation) [2020-MEUR/MW_e] | 0.14 | 0.13 | 0.1 | 0.09 | 0.09 | 0.12 | 0.14 | 0.08 | 0.1
| Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] | 0.23 | 0.05 | 0.04 | 0.04 | 0.03 | 0.05 | 0.05 | 0.03 | 0.04
| Nominal investment (soft costs) [2020-MEUR/MW_e] | 0.09 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.02 | 0.03 | V
| Fixed O&M (*total) [2020-EUR/MW_e/y] | 13600 | 11300 | 9500 | 8100 | 7400 | 10100 | 12400 | 6600 | 8100
| Fixed O&M (land rent) [2020-EUR/MW_e/y] | ctrl: 4400; ctrl: 3900; ctrl: 3100; ctrl: 2500; note: S
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 5.4; ctrl: 50; ctrl: 50; ctrl: 50; ctrl: 50; note: C
| Space requirement (per DC) [1000m2/MW_e] | 15 | 11 | 9.8 | 9.2 | 8.67 |  |  |  |  | B,B1 | 6
| Nominal investment (installation, per DC) [2020-MEUR/MW_e] | 0.11 | 0.1 | 0.08 | 0.07 | 0.07 | 0.1 | 0.11 | 0.06 | 0.08 | V
| Nominal investment (inverter, per DC) [2020-MEUR/MW_e] | 0.08 | 0.02 | 0.02 | 0.01 | 0.01 | 0.02 | 0.03 | 0.01 | 0.01
| Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] | 0.17 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.02 | 0.03
| Nominal investment (pv module, per DC) [2020-MEUR/MW_e] | 0.66 | 0.21 | 0.11 | 0.08 | 0.07 | 0.2 | 0.22 | 0.06 | 0.14
| Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] | 0.06 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02 | V
| Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] | 0.06 | 0.05 | 0.04 | 0.04 | 0.03 | 0.05 | 0.05 | 0.03 | 0.04 | R
| Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] | 10100 | 9000 | 7600 | 6500 | 5900 | 8100 | 9900 | 5300 | 6500
| Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | ctrl: 3500; ctrl: 3100; ctrl: 2500; ctrl: 2000; note: S; ref: 6
| Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | ctrl: 5500; ctrl: 4500; ctrl: 4000; ctrl: 3900; note: P2
| Average annual degradation of full-load hours [] | 0.5% | 0.4% | 0.3% | 0.3% | 0.3% | 0.3% | 0.5% |  |  | A2
| Global horizontal irradiance [MWh/m2/y] | 1068 | 1068 | 1068 | 1068 | 1068 |  |  |  |  | A | 1
| Transposition factor | ctrl: 1.15; ctrl: 1.17; ctrl: 1.17; ctrl: 1.17; ctrl: 1.17; note: E
| Performance ratio (contribution from bifaciality) [] | 0% | 1% | 5% | 5% | 5% |  |  |  |  | H | 3
| Performance ratio (measure of combined losses) [] | ctrl: 81%; ctrl: 86%; ctrl: 95%; ctrl: 96%; ctrl: 97%; note: F
| PV module conversion efficiency [] | 16.5% | 20.5% | 23% | 24.5% | 26% | 20% | 21% |  |  | U | 3
| Inverter lifetime [years] | ctrl: 10; ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; ref: 6
| Sizing factor (DC/AC) [W_e/W_e] | 1.35 | 1.25 | 1.25 | 1.25 | 1.25 |  |  |  |  | D | 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 981.33; ctrl: 1074.62; ctrl: 1187.08; ctrl: 1199.58; ctrl: 1212.07; note: A1, K
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1324.8; ctrl: 1343.28; ctrl: 1483.85; ctrl: 1499.47; ctrl: 1515.09; note: A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 22 Utility-scale PV tracker
Technology |  | PV - renewable power - solar - utility-scale ground mounted, single axis tracking
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 40; ctrl: 40; ctrl: 40; ctrl: 40
Forced outage [] | bar: ctrl to ctrl
| Planned outage [weeks per year] | ctrl: 0; ctrl: 0; ctrl: 0; ctrl: 0
| Technical lifetime [years] | ctrl: 35; ctrl: 40; ctrl: 40; ctrl: 40
| Construction time [years] | ctrl: 0.5; ctrl: 0.5; ctrl: 0.5; ctrl: 0.5
| Space requirement [1000 m2/MW_e] | ctrl: 17.88; ctrl: 15.93; ctrl: 14.96; ctrl: 14.09; note: B,B1; ref: 6
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
Financial data
| Nominal investment (*total) [2020-MEUR/MW_e] |  | 0.65 | 0.45 | 0.38 | 0.35 | 0.6 | 0.7 | 0.29 | 0.47 | M,N,O,Q | 2, 4
| Nominal investment (*total, per DC) [2020-MEUR/MW_e] |  | 0.52 | 0.36 | 0.31 | 0.28 | 0.48 | 0.56 | 0.23 | 0.38 | M,N,O,Q | 2, 4
| Nominal investment (grid connection) [2020-MEUR/MW_e] |  | 0.06 | 0.05 | 0.04 | 0.04 | 0.06 | 0.07 | 0.04 | 0.05
| Nominal investment (inverter) [2020-MEUR/MW_e] |  | 0.03 | 0.02 | 0.02 | 0.01 | 0.03 | 0.03 | 0.01 | 0.02
| Nominal investment (pv modules) [2020-MEUR/MW_e] |  | 0.26 | 0.14 | 0.11 | 0.09 | 0.24 | 0.28 | 0.07 | 0.17
| Nominal investment (tracker related costs) [2020-MEUR/MW_e] |  | 0.09 | 0.07 | 0.06 | 0.06 | 0.08 | 0.09 | 0.05 | 0.07 | T
| Nominal investment (installation) [2020-MEUR/MW_e] |  | 0.13 | 0.1 | 0.09 | 0.09 | 0.12 | 0.14 | 0.07 | 0.1
| Nominal investment (other, i.e. residual balance of plant) [2020-MEUR/MW_e] |  | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.02 | 0.03
| Nominal investment (soft costs) [2020-MEUR/MW_e] |  | 0.05 | 0.04 | 0.04 | 0.03 | 0.04 | 0.05 | 0.03 | 0.04 | V
| Fixed O&M (*total) [2020-EUR/MW_e/y] |  | 12100 | 10400 | 9400 | 9000 | 10900 | 13400 | 8100 | 9900 | P2
| Fixed O&M (land rent) [2020-EUR/MW_e/y] | ctrl: 5300; ctrl: 4800; ctrl: 4400; ctrl: 4100; note: S
Technology-specific data
| Generating capacity for one unit (DC-value) [MW_e] | ctrl: 50; ctrl: 50; ctrl: 50; ctrl: 50; note: C
| Space requirement (per DC) [1000m2/MW_e] | ctrl: 14.3; ctrl: 12.75; ctrl: 11.97; ctrl: 11.28; note: B,B1; ref: 6
| Nominal investment (installation, per DC) [2020-MEUR/MW_e] |  | 0.1 | 0.08 | 0.07 | 0.07 | 0.09 | 0.11 | 0.06 | 0.08 | V
| Nominal investment (inverter, per DC) [2020-MEUR/MW_e] |  | 0.02 | 0.02 | 0.01 | 0.01 | 0.02 | 0.03 | 0.01 | 0.01
| Nominal investment (other, i.e. residual balance of plant, per DC) [2020-MEUR/MW_e] |  | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02
| Nominal investment (pv module, per DC) [2020-MEUR/MW_e] |  | 0.21 | 0.11 | 0.08 | 0.07 | 0.19 | 0.22 | 0.05 | 0.14
| Nominal investment (soft costs, per DC) [2020-MEUR/MW_e] |  | 0.04 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.02 | 0.03 | V
| Nominal investment (tracker related cost, per DC) [2020-MEUR/MW_e] |  | 0.07 | 0.06 | 0.05 | 0.05 | 0.06 | 0.08 | 0.04 | 0.05 | T
| Nominal investment (transformer and grid connection, per DC) [2020-MEUR/MW_e] |  | 0.05 | 0.04 | 0.04 | 0.03 | 0.04 | 0.05 | 0.03 | 0.04 | R
| Fixed O&M (*total, per DC) [2020-EUR/MW_e/y] |  | 9700 | 8300 | 7500 | 7200 | 8700 | 10700 | 6500 | 7900
| Fixed O&M (land rent, per DC) [2020-EUR/MW_e/y] | ctrl: 4200; ctrl: 3800; ctrl: 3500; ctrl: 3300; note: S; ref: 6
| Fixed O&M (other, per DC) [2020-EUR/MW_e/y] | ctrl: 5500; ctrl: 4500; ctrl: 4000; ctrl: 3900; note: P2
| Average annual degradation of full-load hours [] |  | 0.4% | 0.3% | 0.3% | 0.3% | 0.3% | 0.5% |  |  | A2
| Global horizontal irradiance [MWh/m2/y] | ctrl: 1068; ctrl: 1068; ctrl: 1068; ctrl: 1068; note: A; ref: 1
| Transposition factor | ctrl: 1.35; ctrl: 1.35; ctrl: 1.35; ctrl: 1.35; note: E
| Performance ratio (contribution from bifaciality) [] | ctrl: 1%; ctrl: 5%; ctrl: 5%; ctrl: 5%; note: H; ref: 3
| Performance ratio (measure of combined losses) [] | ctrl: 86%; ctrl: 95%; ctrl: 96%; ctrl: 97%; note: F
| PV module conversion efficiency [] |  | 20.5% | 23% | 24.5% | 26% | 20% | 21% |  |  | U | 3
| Inverter lifetime [years] | ctrl: 12.5; ctrl: 15; ctrl: 15; ctrl: 15; ref: 6
| Sizing factor (DC/AC) [W_e/W_e] | ctrl: 1.25; ctrl: 1.25; ctrl: 1.25; ctrl: 1.25; note: D; ref: 5, 6
| Average annual full-load hours (DC-value) [MWh_e/MW_e] | ctrl: 1235.81; ctrl: 1369.71; ctrl: 1379.51; ctrl: 1393.88; note: A1, K
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1544.77; ctrl: 1712.14; ctrl: 1724.39; ctrl: 1742.36; note: A1
Notes:
A. The global irradiation is a measure of the energy resource potential available and is depended on the exact geographical location. The average value in Denmark as determined among 25 measurement stations is 1068 (kWh/m2/y) ± 3.1 %. The best sites demonstrate values around 1100 kWh/m2/y.
A1. The average annual full-load hours are based on the project's initial efficiency, but can be affected negatively by wear and degradation over the system's lifetime.
A2. Generally, the initial efficiceny will decrease throughout the lifetime by wear and degradation. It is common to attribute an annual degradation loss to the system, which depends on maintenance, climatic conditions, etc.
B. The area requirement decreases as the efficiency of PV panels increases.
B1. In 2019 a typical fixed mount PV-plant requires an area of around 1.1 ha/MWp. This includes distance between solar panels, distance to fence, internal roads, transformer stations and monitoring equipment. For single axis tracker its around 1.3 ha/MWp. For residential and commercial PV, the space requirement is based on calculation of the inverted efficiency as rooftop mounting requires no space between panels.
B2. 110 kWp corresponding to a panel area of approximately 400 - 700 m2.
B3. 6.3 kWp corresponding to a panel area of approximately 30-40m2.
C. The peak power of the system is the max. power of the PV modules (DC).
D. The DC/AC shown equals module peak capacity (in Wp) divided by inverter/transformer capacity (Wac,max). The sizing factor is set to the same value for all years . In practice the sizing factor is chosen according to the desired utilisation/loading of the inverter which can also reflect a desire to maximise the energy production from a given (restricted) AC-capacity. Single axis tracker systems can be sized with a smaller inverter relative to fixed tilt systems without loosing too much generation because their peak generation is usually lower.
E. The transposition factor describes the increase in the sunlight energy that can be obtained by tilting the module with respect to horizontal and reduction in received energy when the orientation deviates from South. The TF factor is set to the same value for all years and sizes of the system, as it is not the technical factors of the system, which determine the TF. The factor for tracking systems is about 10 % higher relative to fixed mount systems as the inclination angle can be adjusted during the day.
F. The performance ratio is an efficiency measure which takes the combined losses from incident angle modifer, inverter loss, PV systems losses and non-STC corrections and AC grid losses into account. The Incident Angle Modifier (IAM) loss represents the total yearly solar energy that is reflected from the glass when the angle of incidence is different from the perpendicular (the reflections at a normal incidence is already included in the STC efficiency). PV systems losses and non-STC corrections are calculated by simulating a model-year where corrections are made hour-by-hour due to the fact that the actual operation does not take place under STC conditions. Additionally, electrical losses in cables are included. The inverter loss includes the Maximum Power Point Tracking (MPPT) efficiency and is averaged over typical load levels. An addition to the ratio is the added benefit of having bifacial modules which raise the generation by 5%.
G. PV plants may provide downregulation if generating or upregulation if not generating at maximum capacity. Usually, PV plants would operate at maximum capacity, since this would maximize earnings in the power market under normal conditions.
H. Note that the Performance Ratio is increased gradually from 2020 to 2030 due to technical solutions which lower losses. For utility scale systems, bifacial modules are assumed to have a 20-30% market share in 2020 and 80% in 2030 in Denmark. The effect of bifacial modules are therefore added gradually. Early studies show that bifacial modules have a 5% increased generation relative to monofacial.
I. Not relevant for small and medium size plants.
K. Full load hours (kWh/kWp)= Global horizontal irradiance (kWh/m2/year)*Transposition Factor *Performance ratio (measure of combined losses)
L. Capacity factor = Full load hours / Total number of hours per year (8760 h/y).
M. Market prices for PV systems have been estimated based on interviews with Danish developers in 2021. These prices are differentiated between residential, commercial and utility scale systems.
N. Inflation relative to 2015 has been accounted for with the following values (Samfundsøkonomiske Beregningsforudsætninger, Energistyrelsen): {"real prices (EUR-2015)" : {"2015":1.0,"2016":1.002,"2017":1.014,"2018":1.03,"2019":1.043, "2020":1.062}}
O. The prices analysis contains a forecast of the PV cost in 2020, 2030, 2040 and 2050, which based on learning rates for the module and inverter (25 % and 19% learning rate) and a projection of the cumulated PV capacity based on the IEA Announced Pledges Scenario 2021. A more moderate learning rate of 10% was used for the installation costs, soft costs, transformer costs, grid connection costs and other costs.
P. The cost of O&M includes regular replacement of inverters. The inverter is assumed to have 12.5 year lifetime. The cost of a new inverter is calculated as a yearly cost.
P2. The cost of O&M includes insurance and regular replacement of inverters and land-lease. As the efficiency of the new solar panels increases, the required area per MWp will be lower, thereby lowering the cost of rented land. The development of insurance costs, self-consumption costs, fixed O&M per MWp costs are assumed to have a 10% learning rate, whereas the inverter replacement costs have a 19% learning rate.
Q. The upper bound for cost uncertainty is calculated by using the estimated global PV capacity from the IEA Stated Policies Scenario 2021 but with a higher starting point in 2020 and a lower module learning rate of 12.5%. The lower bound is calculated using the estimated global PV capacity from the IEA Net Zero Scenario 2021.
R. Transformer and grid connection costs tend to vary depending on the location of the plant relative to the grid as well as size of the plant. This specific cost of utility scale is based on connection at 50/60 kV.
S. O&M cost of rented land calculations are made with the assumption that the plant ha/MWp ratio is 1.1. The projected increase in module efficiency will result in a decreased ha/MWp ratio which then decreases the cost of rent of land towards 2050. For single axis tracker systems, the ratio used in 2020 is 1.3 ha/MWp. The cost of rented land is assumed constant but decreases with increasing solar cell efficiency. It is not taken into account that favorable PV-site locations could potentially rise in costs as locations become scarse.
T. The added tracker cost is based on interviews with Danish manufacturers.
U. The efficiency is a market average of commercial modules. Modules with above 21% efficiency are, as of 2019, commercially available but not common in PV projects. The market development towards 2030 is projected to shift to back contact n-type mono- Si cells and silicon heterojunction(HJT) n-type mono-Si cells which both have higher efficiencies.
V. The soft cost includes permits, surveys and studies on grid level, geotechnical analysis, legal costs, envionmental costs, planning costs. The installation cost covers all physical installation, electrical hardware, mechanical mounting system.
W. "Equipment" covers PV module, inverter, transformer and grid connection. "Other" covers soft costs and other costs.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Peter Riddersholm Wang, DMI Teknisk Rapport 13-08, Referenceværdier: Måneds- og årsværdier for stationer 2001 - 2010, Danmark for temperatur, relativ luftfugtighed, vindhastighed, globalstråling og nedbør.
2. "World Energy Outlook". IEA. 2021.
3. " Photovoltaics report". Fraunhofer. 27 July 2021.
4. "Global Market Outlook For Solar Power 2021 - 2025". SolarPower Europe. July 2021.
5. PV Tech. (4. Juli 2017). Hentet fra https://www.pv-tech.org/products/helioslites-disruptive-1.5-axis-pv-tracker
6. Interviews with Danish developers and suppliers in the summer 2021.

## 23 Wave Energy
Technology |  | Wave power - renewable power - wave - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ref: [1, 1, 4, 4]
| Generating capacity for one unit [MW_e] | lower: 2; upper: 50; lower: 50; upper: 500
| Technical lifetime [years] | ctrl: 10; ctrl: 20; ctrl: 25; ctrl: 30; ref: 4
| Construction time [years] | ctrl: 3.5; ctrl: 3.5; ctrl: 3.5; note: C; ref: 4
| Construction time [years] | lower: 3; upper: 4; lower: 3; upper: 4
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | ctrl: 1.6; note: [A, B]; ref: [2, 2, 2, 3]
| Nominal investment (*total) [2015-MEUR/MW_e] | lower: 3.8; upper: 9
| Variable O&M (*total) [2011-EUR/MWh_e] | ctrl: 20; ctrl: 15; ctrl: 10; ctrl: 7; ref: 4
Technology-specific data
| Availability [] | ctrl: 90%; ctrl: 95%; ctrl: 97%; ctrl: 98%; ref: 4
| Length of installation of one power plant [km] | ref: [1, 1, 4, 4]
| Length of installation of one power plant [km] | lower: 0.2; upper: 5; lower: 5; upper: 100
| Average annual full-load hours [MWh_e/MW_e] | ctrl: 1500; ctrl: 2500; ctrl: 3500; ctrl: 4500; ref: 4
Notes:
A. The cost presented provides an estimate for what capital cost and operating costs of wave power converters might be in the future assuming all R&D challenges have been overcome, that economics of scale have been realized and that efficiencies in production and operation due to the learning curve effect have been achieved.
B. Cost data are the same as in the 2010 catalogue, however inflated from price level 2008 to 2011 by multiplying with a general inflation factor 1.053
C. Much dependent on plant size and location.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Wave Net final report, Project no. ERK5 - CT -1999-20001 (2000 - 2003)
2. "Energy Technology Perspectives 2008", International Energy Agency, 2008.
3. "Energy Technology Perspectives 2010", International Energy Agency, 2010.
4. Danish Wave Energy Association, 2012

## 40 Comp. hp, airsource 1 MW
Technology |  | Heat pump, air source - heat pump - electricity - small
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 1 | 1 | 1 | 1 | 1 | 0.3 | 1.5 | 0.2 | 1.5
| Heat efficiency (net, annual average) [] | 290% | 295% | 300% | 310% | 315% | 275% | 335% | 285% | 355% | [A, A1, B, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 255% | 260% | 265% | 275% | 280% | 240% | 300% | 250% | 320% | [A, A1, B, C] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | E | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | [F, G] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 1 | 1 | 1 | 1 | 1 | 0.7 | 2 | 0.7 | 2 | Q | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | H | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | H | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [H, J] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | H | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [H, I] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 1.43 | 1.43 | 1.33 | 1.33 | 1.33 | 0.95 | 1.9 | 0.95 | 1.9 | [A, K, L, P, Q] | [1, 14, 15]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 1.07 | 1.07 | 1 | 1 | 1 | 0.71 | 1.43 | 0.71 | 1.43 | A | [1, 14, 15]
| Nominal investment (grid connection) [2015-MEUR/MW_e] | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.19 | 0.02 | 0.19 | K | [1, 14, 15]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.26 | 0.26 | 0.24 | 0.24 | 0.24 | 0.17 | 0.19 | 0.17 | 0.19 | A | [1, 14, 15]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.17 | 3.17 | 2.17 | 3.17 |  | [1, 14, 15]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [E, N] | [1, 14, 15]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 2.69 | 2.69 | 2.69 | 2.69 | 2.69 | 2.17 | 3.17 | 2.17 | 3.17 | M | [1, 14, 15]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | M | [1, 14, 15]
| Startup cost [2015-EUR/MW_h/startup] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | O | 15
Notes:
A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Includes energy consumption for defrosting and auxiliary electricity consumption.
C. Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
D. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
E. Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
F. Does not include tendering and regulatory approvals.
G. The development within construction time will depend on future production figures and standardization of plants.
H. The regulation ablility will depend on the future markets for regulation services.
I. Cold start of time is starting a heat pump where stand by heating has not been applied
J. Operation at part load will usually increase COP but also variable O&M costs
K. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
L. Land is usually owned by the company
M. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
N. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
O. 1/4 MWh-heat per MW is lost during startup
P. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 15 % as compontents must be rated for higher pressure levels
Q. Including land for air coolers
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, airsource 3 MW
Technology |  | Heat pump, air source - heat pump - electricity - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 3 | 3 | 3 | 3 | 3 | 1.5 | 5 | 1.5 | 5
| Heat efficiency (net, annual average) [] | 340% | 350% | 360% | 365% | 370% | 320% | 370% | 330% | 380% | [A, A1, B, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 310% | 315% | 320% | 330% | 340% | 290% | 330% | 300% | 350% | [A, A1, B, C] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | E | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.5 | 1 | 0.4 | 1 | [F, G] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 1.2 | 0.5 | 1.2 | Q | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 100% | 5% | 100% | H | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | H | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [H, J] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | H | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [H, I] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.95 | 0.95 | 0.86 | 0.86 | 0.86 | 0.76 | 1.43 | 0.67 | 1.43 | [A, K, L, P, Q] | [1, 14, 15]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.76 | 0.76 | 0.68 | 0.68 | 0.68 | 0.61 | 1.14 | 0.53 | 1.14 | A | [1, 14, 15]
| Nominal investment (grid connection) [2015-MEUR/MW_e] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.14 | 0.01 | 0.14 | K | [1, 14, 15]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.17 | 0.17 | 0.15 | 0.15 | 0.15 | 0.14 | 0.14 | 0.12 | 0.14 | A | [1, 14, 15]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.19 | 2.19 | 2.51 | 2.19 | 2.67 | 2.19 | 3.69 | 2.19 | 2.19 |  | [1, 14, 15]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [E, N] | [1, 14, 15]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 2.19 | 2.19 | 2.51 | 2.19 | 2.67 | 2.19 | 3.69 | 2.19 | 2.19 | M | [1, 14, 15]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | M | [1, 14, 15]
| Startup cost [2015-EUR/MW_h/startup] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | O | 15
Notes:
A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Includes energy consumption for defrosting and auxiliary electricity consumption.
C. Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
D. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
E. Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
F. Does not include tendering and regulatory approvals.
G. The development within construction time will depend on future production figures and standardization of plants.
H. The regulation ablility will depend on the future markets for regulation services.
I. Cold start of time is starting a heat pump where stand by heating has not been applied
J. Operation at part load will usually increase COP but also variable O&M costs
K. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
L. Land is usually owned by the company
M. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
N. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
O. 1/4 MWh-heat per MW is lost during startup
P. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 10 % as compontents must be rated for higher pressure levels
Q. Including land for air coolers
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, airsource 10 MW
Technology |  | Heat pump, air source - heat pump - electricity - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 5 | 20
| Heat efficiency (net, annual average) [] | 380% | 380% | 385% | 390% | 390% | 360% | 400% | 360% | 410% | [A, A1, B, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 350% | 350% | 355% | 360% | 360% | 330% | 370% | 330% | 380% | [A, A1, B, C] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | E | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.5 | 1 | 0.4 | 1 | [F, G] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 1 | 0.4 | 1 | Q | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 100% | 5% | 100% | H | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | H | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [H, J] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | H | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [H, I] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.86 | 0.86 | 0.76 | 0.76 | 0.76 | 0.67 | 1.14 | 0.67 | 1.14 | [A, K, L, P, Q] | [1, 14, 15]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.68 | 0.68 | 0.61 | 0.61 | 0.61 | 0.53 | 0.91 | 0.53 | 0.91 | A | [1, 14, 15]
| Nominal investment (grid connection) [2015-MEUR/MW_e] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.11 | 0.01 | 0.11 | K | [1, 14, 15]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.15 | 0.15 | 0.14 | 0.14 | 0.14 | 0.12 | 0.11 | 0.12 | 0.11 | A | [1, 14, 15]
| Variable O&M (*total) [2015-EUR/MWh_h] | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1 | 2.69 | 1 | 2.69 |  | [1, 14, 15]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [E, N] | [1, 14, 15]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1.69 | 1.69 | 1.69 | 1.69 | 1.69 | 1.5 | 2.69 | 1.5 | 2.69 | M | [1, 14, 15]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | M | [1, 14, 15]
| Startup cost [2015-EUR/MW_h/startup] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | O | 15
Notes:
A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Includes energy consumption for defrosting and auxiliary electricity consumption.
C. Total efficiency, net (%), name plate is at an ambient temperature of -1 °C. District heating temperatures are 35 °C return and 70 °C forward.
D. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
E. Auxiliary electricity consumption is included in the Total efficiency. Electricity for fans constitute appr. 0.3 %. Cost for electricity is therefore not accounted for in variable O&M
F. Does not include tendering and regulatory approvals.
G. The development within construction time will depend on future production figures and standardization of plants.
H. The regulation ablility will depend on the future markets for regulation services.
I. Cold start of time is starting a heat pump where stand by heating has not been applied
J. Operation at part load will usually increase COP but also variable O&M costs
K. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
L. Land is usually owned by the company
M. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
N. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
O. 1/4 MWh-heat per MW is lost during startup
P. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
Q. Including land for air coolers
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, excess heat 1 MW
Technology |  | Heat pump, industrial excess heat - heat pump - electricity - small
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 1 | 1 | 1 | 1 | 1 | 0.3 | 1.5 | 0.2 | 1.5
| Heat efficiency (net, annual average) [] | 410% | 420% | 430% | 440% | 450% | 410% | 450% | 410% | 480% | [A, A1, C, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 400% | 410% | 420% | 430% | 440% | 400% | 430% | 400% | 450% | [A, A1, B, D] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | D | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | [E, F] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.2 |  | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | G | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | G | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [G, I] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [G, H] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 1.24 | 1.24 | 1.14 | 1.14 | 1.14 | 0.95 | 1.9 | 0.95 | 1.9 | [A, J, K, O] | [1, 14, 15]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.93 | 0.93 | 0.86 | 0.86 | 0.86 | 0.71 | 1.43 | 0.71 | 1.43 | A | [1, 14, 15]
| Nominal investment (grid connection) [2015-MEUR/MW_e] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.19 | 0.02 | 0.19 | J | [1, 14, 15]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.22 | 0.22 | 0.21 | 0.21 | 0.21 | 0.17 | 0.19 | 0.17 | 0.19 | A | [1, 14, 15]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.69 | 2.69 | 2.69 | 3.09 | 3.17 | 1.69 | 2.69 | 2.69 | 3.17 |  | [1, 14, 15]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [D, M] | [1, 14, 15]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 2.69 | 2.69 | 2.69 | 3.09 | 3.17 | 1.69 | 2.69 | 2.69 | 3.17 | L | [1, 14, 15]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | L | [1, 14, 15]
| Startup cost [2015-EUR/MW_h/startup] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | N | 15
Notes:
A. Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E. Does not include tendering and regulatory approvals.
F. The development within construction time will depend on future production figures and standardization of plants.
G. The regulation ability will depend on the future marktes for regulation services.
H. Cold start of time is starting a heat pump where stand by heating has not been applied
I. Operation at part load will usually increase COP but also variable O&M costs
J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K. Land is usually owned by the company
L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N. 1/4 MWh-heat per MW is lost during startup
O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 15 % as compontents must be rated for higher pressure levels
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, excess heat 3 MW
Technology |  | Heat pump, industrial excess heat - heat pump - electricity - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 3 | 3 | 3 | 3 | 3 | 1.5 | 5 | 1.5 | 5
| Heat efficiency (net, annual average) [] | 460% | 470% | 480% | 490% | 500% | 450% | 490% | 460% | 520% | [A, A1, C, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 450% | 460% | 470% | 480% | 490% | 440% | 480% | 450% | 510% | [A, A1, B, D] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | D | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | [E, F] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.1 | 0.03 | 0.1 |  | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | G | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | G | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [G, I] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [G, H] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.86 | 0.86 | 0.76 | 0.76 | 0.76 | 0.67 | 1.14 | 0.67 | 1.14 | [A, J, K, O] | [1, 14, 15]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.68 | 0.68 | 0.61 | 0.61 | 0.61 | 0.53 | 0.91 | 0.53 | 0.91 | A | [1, 14, 15]
| Nominal investment (grid connection) [2015-MEUR/MW_e] | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.11 | 0.01 | 0.11 | J | [1, 14, 15]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.15 | 0.15 | 0.14 | 0.14 | 0.14 | 0.12 | 0.11 | 0.12 | 0.11 | A | [1, 14, 15]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.19 | 2.19 | 2.51 | 2.19 | 2.67 | 2.19 | 2.19 | 2.17 | 2.19 |  | [1, 14, 15]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [D, M] | [1, 14, 15]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 2.19 | 2.19 | 2.51 | 2.19 | 2.67 | 2.19 | 2.19 | 2.17 | 2.19 | L | [1, 14, 15]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | L | [1, 14, 15]
| Startup cost [2015-EUR/MW_h/startup] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | N | 15
Notes:
A. Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E. Does not include tendering and regulatory approvals.
F. The development within construction time will depend on future production figures and standardization of plants.
G. The regulation ability will depend on the future marktes for regulation services.
H. Cold start of time is starting a heat pump where stand by heating has not been applied
I. Operation at part load will usually increase COP but also variable O&M costs
J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K. Land is usually owned by the company
L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N. 1/4 MWh-heat per MW is lost during startup
O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 10 % as compontents must be rated for higher pressure levels
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, excess heat 10 MW
Technology |  | Heat pump, industrial excess heat - heat pump - electricity - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 5 | 20
| Heat efficiency (net, annual average) [] | 510% | 520% | 530% | 540% | 550% | 500% | 530% | 510% | 570% | [A, A1, C, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 500% | 510% | 520% | 530% | 540% | 490% | 520% | 500% | 560% | [A, A1, B, D] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | D | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 1 | 0.3 | 1 | [E, F] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.06 | 0.02 | 0.06 |  | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | G | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | G | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [G, I] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | G | [9, 14, 15]
| Cold start-up time [hours] | 1 | 1 | 1 | 1 | 1 | 0.2 | 1 | 0.2 | 1 | [G, H] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.67 | 0.67 | 0.57 | 0.57 | 0.57 | 0.48 | 0.95 | 0.48 | 0.95 | [A, J, K, O] | [1, 14, 15]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.53 | 0.53 | 0.46 | 0.46 | 0.46 | 0.38 | 0.76 | 0.38 | 0.76 | A | [1, 14, 15]
| Nominal investment (grid connection) [2015-MEUR/MW_e] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.1 | 0.01 | 0.1 | J | [1, 14, 15]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.12 | 0.12 | 0.1 | 0.1 | 0.1 | 0.09 | 0.1 | 0.09 | 0.1 | A | [1, 14, 15]
| Variable O&M (*total) [2015-EUR/MWh_h] | 1.69 | 1.69 | 2.01 | 2.09 | 1.69 | 1.19 | 2.19 | 1.69 | 2.67 |  | [1, 14, 15]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [D, M] | [1, 14, 15]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1.69 | 1.69 | 2.01 | 2.09 | 1.69 | 1.19 | 2.19 | 1.69 | 2.67 | L | [1, 14, 15]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 5000 | L | [1, 14, 15]
| Startup cost [2015-EUR/MW_h/startup] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | N | 15
Notes:
A. Based on cooling water that is cooled from 25 to 15 °C. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
A1. Performance data regarding ambient air and industrial waste heat are based on typical supply temperatures of decentral district heating systems with an annual average return/forward temperature of 35 °C / 70 °C (it varies over the year). It is assumed that the heat pumps only cover 85 % of the annual heat demand, meaning that the heat pumps co-produce with peak load units during the coldest periods. This mean that the forward temperature of the heat pump can be kept at around 70 °C during the coldest periods or even lowered.
B. Total efficiency, net (%), name plate is at district heating temperatures of 35 °C return and 70 °C forward.
C. Annual average at 85 % heat production of total demand utilizing coproduction at peak demands with reduced output temperatur from heat pump. DH temperatures are 35 °C return and 70 °C forward.
D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E. Does not include tendering and regulatory approvals.
F. The development within construction time will depend on future production figures and standardization of plants.
G. The regulation ability will depend on the future marktes for regulation services.
H. Cold start of time is starting a heat pump where stand by heating has not been applied
I. Operation at part load will usually increase COP but also variable O&M costs
J. It is assumed that heat pumps is connected with limited access like electrical boilers. Upper values regarding uncertainty assume that installations must pay for full access
K. Land is usually owned by the company
L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N. 1/4 MWh-heat per MW is lost during startup
O. At district heating temperatures of 40-80 °C, the specific investment is expected to increase by 5 % as compontents must be rated for higher pressure levels
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Comp. hp, seawater 20 MW
Technology |  | Heat pump, sea water - heat pump - electricity - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 20 | 20 | 20 | 20 | 20 | 10 | 50 | 10 | 100
| Heat efficiency (net, annual average) [] | 370% | 370% | 370% | 380% | 380% | 360% | 380% | 370% | 390% | [A, C, D] | [1, 14, 15]
| Heat efficiency (net, name plate) [] | 340% | 340% | 340% | 350% | 350% | 330% | 350% | 340% | 360% | [A, B, D] | [1, 14, 15]
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | D | [1, 14, 15]
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% |  | [1, 14, 15]
| Planned outage [weeks per year] | 1 | 1 | 1 | 1 | 1 | 0.5 | 2 | 0.5 | 2 |  | [1, 14, 15]
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 |  | [1, 9, 10, 14, 15]
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 0.7 | 1.5 | 0.5 | 1.5 | [E, F] | [9, 14, 15]
| Space requirement [1000 m2/MW_h] | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.06 | 0.02 | 0.06 | O | [15, 18]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 5% | 5% | 5% | 5% | 5% | 5% | 50% | 5% | 50% | G | [1, 9, 14, 15]
| Secondary regulation (of full load, per minute) [] | 10% | 10% | 10% | 10% | 10% | 10% | 100% | 10% | 100% | G | [1, 9, 14, 15]
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | [G, I] | [1, 9, 14, 15]
| Warm start-up time [hours] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.3 | 0.1 | 0.3 | G | [9, 14, 15]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 2 | [G, H] | [9, 14, 15]
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.48 | 0.48 | 0.38 | 0.38 | 0.38 | 0.29 | 1 | 0.29 | 1 | [A, J, K, O] | [1, 14, 15]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.4 | 0.4 | 0.32 | 0.32 | 0.32 | 0.24 | 0.85 | 0.24 | 0.85 | A | [1, 14, 15]
| Nominal investment (grid connection) [2015-MEUR/MW_e] | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.1 | J | [1, 14, 15]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.04 | 0.05 | 0.04 | 0.05 | A | [1, 14, 15]
| Variable O&M (*total) [2015-EUR/MWh_h] | 1.19 | 1.19 | 1.51 | 1.59 | 1.67 | 1.19 | 1.69 | 1.47 | 1.19 |  | [1, 14, 15]
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M | [1, 14, 15]
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1.19 | 1.19 | 1.51 | 1.59 | 1.67 | 1.19 | 1.69 | 1.47 | 1.19 | L | [1, 14, 15]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 4000 | 4000 | 4000 | 4000 | 4000 | 2000 | 5000 | 2000 | 5000 | L | [1, 14, 15]
| Startup cost [2015-EUR/MW_h/startup] | 10 | 10 | 10 | 10 | 10 | 5 | 20 | 2 | 20 | N | 15
Notes:
A. Actual development within COP optimization and reduced investment cost depends on the development in fuel and electricity prices.
B. Total efficiency, net (%), name plate is at a sea water temperature of 4 °C and district heating temperatures of 40 °C return and 80 °C forward.
C. Annual average is at varying sea water temperatures and district heating temperatures of 40 °C return and 80 °C forward.
D. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M
E. Does not include tendering and regulatory approvals.
F. The development within construction time will depend on future production figures and standardization of plants.
G. The regulation ability will depend on the future marktes for regulation services.
H. Cold start of time is starting a heat pump where stand by heating has not been applied
I. Operation at part load will usually increase COP but also variable O&M costs
J. It is assumed that heat pumps is connected to existing power stations
K. Land is usually owned by the company
L. O&M regard the heat pump it self including auxiliary equipment, building etc. for the heat pump. The costs does not include O&M for the entire district heating network, peak load or back up units, administration regarding end users etc.
M. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M
N. 1/4 MWh-heat per MW is lost during startup
O. Regards heat pumps that are installed at existing power plants utilizing existing infra structure such as power supply, seawater intake, DH pipes etc. For stand alone plants it is estimated that the total investment is around the upper uncertainty in the table.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, Støchkel, Paaske, Clausen, 2017, see https://ens.dk/sites/ens.dk/files/Varme/drejebog_for_store_varmepumper.pdf
2. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, Sørensen, Paaske, Jacobsen, Hofmeister, 2013
3. Absorption chillers and heat pumps, Keith E. Herold, Reinhard Radermacher and Sanford A. Klein, 1996
4. Scandinavian Energy Group, 2015, Conversation
5. Advansor, 2015, Conversation
6. Hybrid Energi, 2015, Conversation
7. Innoterm, 2015, Conversation
8. Cronborg, 2015, Conversation
9. Johnson Controls, 2019, Conversation
10. Teknologisk Institut, 2015, 2019, Conversation
11. Energinet.dk, 2015, Conversation
12. IEA 2012, Energy Technology Perspectives, 2012
13. Store varmepumper i fjernvarmen - driftserfaringer, Flørning, Carøe, Nielsen, Støchkel, 2019
14. IES/Victor DST, 2019, Conversation
15. PlanEnergi, 2019, practical experience from installed plants
16. DMI, 2019
17. Danfoss, 2019, Conversation
18. Varmeværket Bjerringbro, Vejen Varmeværk, Skjern Papirfabrik, Høje Taastrup Fjernvarme, Rødkærsbro Kraftvarmeværk, Kalundborg Forsyning, Rye Kraftvarmeværk, Broager Fjernvarmeselskab, Sig Varmeværk, Fensmark Fjernvarme, Slagslunde Fjernvarme, Farum Fjernvarme, FFV Energi & Miljø, Karup Varmeværk, Støvring Kraftvarmeværk, Skagen Varmeværk, Strandby Varmeværk

## 40 Absorption heat pump, DH
Technology |  | Absorption heat pump - heat pump - heat - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 12 | 12 | 12 | 12 | 12 | 20 | 12 | 30 | [A, A1] | 13
| Heat efficiency (net, annual average) [] | 170% | 171% | 173% | 175% | 170% | 180% | 170% | 180% | B | 4
Heat efficiency (net, name plate) []
| Auxiliary Electricity consumption (share of heat gen.) [] | 1% | 1% | 1% | 1% | 1% | 3% | 1% | 3% | E | 3
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 1% | 0% | 1% | C
| Planned outage [weeks per year] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 15 | 30 | 15 | 30 |  | 3
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.7 | 0.3 | 0.7
| Space requirement [1000 m2/MW_h] | 0.01 | 0.01 | 0 | 0 | 0 | 0.01 | 0 | 0.01
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
| Minimum load (of full load) [] | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10%
| Warm start-up time [hours] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 2 | 0.25 | 2
Environment
| SO2 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.6 | 0.56 | 0.51 | 0.46 | 0.4 | 0.8 | 0.4 | 0.8 | [A, A1] | 3
| Nominal investment (equipment) [2015-MEUR/MW_h] | 50 | 50 | 50 | 50 | 30 | 70 | 30 | 70 |  | 3
| Nominal investment (installation) [2015-MEUR/MW_h] | 50 | 50 | 50 | 50 | 30 | 70 | 30 | 70 |  | 3
| Variable O&M (*total) [2015-EUR/MWh_h] | 0.9 | 0.98 | 1.25 | 1.43 | 1 | 2.5 | 1.4 | 0.3
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0.6 | 0.7 | 1 | 1.2 | 0.7 | 2.1 | 1.2 | 0 | E
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 0.3 | 0.28 | 0.25 | 0.23 | 0.3 | 0.4 | 0.2 | 0.3 |  | 3
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 2000 | 2000 | 2000 | 1000 | 3000 | 1000 | 3000 |  | 3
Notes:
A. The heat pump itself only represents a small part of the total investment. Depending on size the heat pump typically represents 0.2 MEUR per. MW heating (excluding drive energy).
A1. Capacity is excluding drive energy.
B. The heat is assumed delivered at 80 °C in 2015 and 60 °C in 2050
C. May vary depending on availability of heat source
D. May vary depending on specific type, heat source etc.
E. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
3. Drejebog til store varmepumpeprojekter i fjernvarmesystemet, 2014, see http://www.planenergi.dk/varmepumper/
4. Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer, 2013
13. Scandinavian Energy Group, 2015

## 40 co2. hp, seawater 50-100 MW
Technology |  | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 65 | 65 | 65 | 65 | 65 | 30 | 150 | 30 | 300 | A,B, M | 1
| Heat efficiency (net, annual average) [] | 301% | 301% | 301% | 311% | 311% | 290% | 310% | 300% | 320% | C, D, F, M, V | 1
| Heat efficiency (net, name plate) [] | 320% | 320% | 320% | 330% | 330% | 310% | 330% | 320% | 340% | C, D, F, M | 1
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.9% | 2.9% | 2.9% | 2.9% | 2.9% | 2.9% | 2.9% | 2.9% | 2.9% | E, F, M | 1
| Forced outage [] | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 0% | 5% | M | 1
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 | M | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 15 | 40 | 15 | 40 | G,M | 1
| Construction time [years] | 2 | 2 | 2 | 2 | 2 | 1.5 | 3 | 1 | 3 | H, I, M | 1
| Space requirement [1000 m2/MW_h] | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.06 | 0.02 | 0.06 | M | 1
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 65% | 65% | 65% | 65% | 65% | 65% | 100% | 65% | 100% | J, K, M | 1
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | J, K, M | 1
| Minimum load (of full load) [] | 25% | 25% | 25% | 25% | 25% | 10% | 50% | 10% | 50% | K, L, M | 1
| Warm start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.75 | 0.25 | 0.75 | K, N, M | 1
| Cold start-up time [hours] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 1 | 0.25 | 1 | K, O, M | 1
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2020-MEUR/MW_h] | 0.94 | 0.94 | 0.89 | 0.84 | 0.8 | 0.79 | 1.4 | 0.65 | 1.4 | A, M, R | 1
| Nominal investment (seawater system) [2020-MEUR/MW_h] | 0.2 | 0.2 | 0.19 | 0.18 | 0.17 | 0.15 | 0.3 | 0.14 | 0.3 | M, R | 1
| Nominal investment (equipment) [2020-MEUR/MW_h] | 0.57 | 0.57 | 0.54 | 0.52 | 0.49 | 0.45 | 0.86 | 0.4 | 0.86 | M, R | 1
| Nominal investment (installation) [2020-MEUR/MW_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M, R | 1
| Nominal investment (other) [2020-MEUR/MW_h] | 0.16 | 0.16 | 0.15 | 0.14 | 0.14 | 0.13 | 0.24 | 0.11 | 0.24 | M, R | 1
| Variable O&M (*total) [2020-EUR/MWh_h] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.5 | 1.98 | 0.5 | 1.98 | M, R, S | 1
| Variable O&M (electricity cost) [2020-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M, P | 1
| Variable O&M (other O&M) [2020-EUR/MWh_h] | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.5 | 1.98 | 0.5 | 1.98 | M, R, S | 1
| Fixed O&M (*total) [2020-EUR/MW_h/y] | 2047.35 | 2047.35 | 2047.35 | 2047.35 | 2047.35 | 1485.15 | 2970.3 | 1485.15 | 2970.3 | M, R | 1
| Startup cost [2020-EUR/MW_h/startup] | 4.95 | 4.95 | 4.95 | 4.95 | 4.95 | 2.97 | 14.85 | 2.97 | 14.85 | M, Q | 1
Technology-specific data
| Nominal investment (grid connection fee) [2020-MEUR/MW_h] | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.01 | 0.08 | 0.03 | 0.08 | M, T | 1
| Nominal investment (heatpump building) [2020-MEUR/MW_h] | 0.11 | 0.11 | 0.1 | 0.1 | 0.09 | 0.09 | 0.16 | 0.05 | 0.16 | M, T | 1
| Nominal investment (seawater connection) [2020-MEUR/MW_h] | 0.08 | 0.08 | 0.08 | 0.08 | 0.07 | 0.07 | 0.13 | 0.04 | 0.13 | M, T | 1
| Nominal investment (seawater intake) [2020-MEUR/MW_h] | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.03 | 0.08 | M, T | 1
| Nominal investment (seawater piping) [2020-EUR/m] | 1663.47 | 1663.47 | 1580.3 | 1497.13 | 1413.95 | 1413.95 | 2495.21 | 831.74 | 2495.21 | M, T | 1
Notes:
A. Design temperatures are 4 °C seawater and DH temperatues of 70/33 °C.
B. 45 MW at 1 °C seawater, 64,5 at 4 °C seawater (the design temperature), and 68,4 MW at 14 °C seawater.
C. Actual development within COP optimization and reduced investment cost depend on the development in fuel and electricity prices.
D. Name plate efficiency is at 4 °C seawater temperature and DH temperatures are 70/33 °C. Total efficiency is in the range of 2,4 to 3,6 depending on the temperature of the seawater and DH. The plant is not in use in the summer period, otherwise, the efficiency could have been even higher.
E. The primary auxililary electricity consumption is related to the seawater pumps.
F. Auxiliary electricity consumption is included in the Total efficiency. Cost for electricity is therefore not accounted for in variable O&M.
G. Tecnical lifetime is calculated with an outage time of 3 month per year.
H. Does not include tendering and regulatory approvals.
I. The development within construction time will depend on future production figures and standardization of plants.
J. Note that this is only valid for upregulation (i.e. load increase of the heat pump). Downregulation (i.e. load reduction on the heat pump) is at a lower rate, however, this can be compesated by other units in the portfolio.
K. CO2 heat pumps regulate a lot faster than e.g. ammonia. The regulation ability will depend on the future markets for regulation services.
L. This is the continous minimum load with only 1 of 2 HP's enabled.
M. All inputs are based on a single case, DIN Forsyning Heat Pump in Esbjerg.
N. The warm start-up time is guaranteed to take 0,5 hours but it is, however, expected to take 0,2 hours.
O. Cold start-up time includes starting a heat pump where stand by heating has not been applied.
P. All consumption of electricity is included in the Total eff., also auxiliary electricity consumption. Cost for electricity is therefore not accounted for in variable O&M. DH distribution system is not included.
Q. 1/4 MWh-heat per MW is lost during startup
R. The forecast for future prices is an estimate since this is the first CO2 heat pump plant in this size.
S. The CO2 heat pumps are made with magnetic barrings and are oilfree, therefore the O&M are lower compared to traditional heat pumps
T. The price is also included in nominal investment (equipment)
V. The heat pumps produce heating at a higher temperature compared to Name plate several months of the year therefore the Name plate COP is higher than the yearly COP.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Interview with DIN Forsyning

## 41 Electric boiler, small
Technology |  | Electric boiler - boiler - electricity - small
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2030 | 2030 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 5 | 5 | 5 | 5 | 1 | 25 |  |  | 1 | 25
| Heat efficiency (net, name plate) [] | 98% | 99% | 99% | 99% | 98% | 99% |  |  | 99% | 99%
| Heat efficiency (net, annual average) [] | 98% | 99% | 99% | 99% | 98% | 99% |  |  | 99% | 99%
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.5% | 0.5% | 0.5% | 0.5% | 0.1% | 0.5% |  |  | 0.1% | 0.5%
| Forced outage [] | 1% | 1% | 1% | 1% | 0.5% | 1% |  |  | 0.5% | 1%
| Planned outage [weeks per year] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  | 0.2 | 0.2
| Technical lifetime [years] | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 20 | 20
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 |  |  | 0.5 | 1
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 100% | 100% | 100% | 100% | 100% | 100% |  |  | 100% | 100%
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% | 100% | 100% |  |  | 100% | 100%
Minimum load (of full load) [] | bar: ctrl to upper; lower to upper
| Warm start-up time [hours] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01
| Cold start-up time [hours] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 |  |  | 0.08 | 0.08
Environment
SO2 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.15 | 0.15 | 0.14 | 0.13 | 0.1 | 0.25 |  |  | 0.1 | 0.25
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.12 | 0.12 | 0.11 | 0.1 | 0.08 | 0.2 |  |  | 0.08 | 0.2
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.05 |  |  | 0.02 | 0.05
| Variable O&M (*total) [2015-EUR/MWh_h] | 0.8 | 0.9 | 1 | 1 | 0.5 | 0.9 |  |  | 0.5 | 1
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0.3 | 0.3 | 0.5 | 0.6 | 0.1 | 0.3 |  |  | 0.1 | 0.6
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.5 |  |  | 0.3 | 0.5
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 1100 | 1070 | 1020 | 920 | 1000 | 1100 |  |  | 900 | 1000
Technology-specific data
| Startup cost [2015-EUR/MW_h/startup] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Notes:
A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
D. The installation costs include costs for electrical integration & grid connection fees.
E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Tjæreborg Industri, 2016
2. Parat, unknown date, Brochure High Voltage Electrode Boiler, available at http://parat.no/media/201154/Electrode-Boiler-web.pdf

## 41 Electric boiler, large
Technology |  | Electric boiler - boiler - electricity - large
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2030 | 2030 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 5 | 5 | 5 | 5 | 1 | 25 |  |  | 1 | 25
| Heat efficiency (net, name plate) [] | 98% | 99% | 99% | 99% | 98% | 99% |  |  | 99% | 99%
| Heat efficiency (net, annual average) [] | 98% | 99% | 99% | 99% | 98% | 99% |  |  | 99% | 99%
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.5% | 0.5% | 0.5% | 0.5% | 0.1% | 0.5% |  |  | 0.1% | 0.5%
| Forced outage [] | 1% | 1% | 1% | 1% | 0.5% | 1% |  |  | 0.5% | 1%
| Planned outage [weeks per year] | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 |  |  | 0.2 | 0.2
| Technical lifetime [years] | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 20 | 20
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 |  |  | 0.5 | 1
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 100% | 100% | 100% | 100% | 100% | 100% |  |  | 100% | 100%
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% | 100% | 100% |  |  | 100% | 100%
Minimum load (of full load) [] | bar: ctrl to upper; lower to upper
| Warm start-up time [hours] | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 |  |  | 0.01 | 0.01
| Cold start-up time [hours] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 |  |  | 0.08 | 0.08
Environment
SO2 [g/GJ_i]
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.07 | 0.07 | 0.06 | 0.06 | 0.02 | 0.17 |  |  | 0.02 | 0.17
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.06 | 0.06 | 0.05 | 0.05 | 0.02 | 0.14 |  |  | 0.02 | 0.14
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0.03 |  |  | 0 | 0.03
| Variable O&M (*total) [2015-EUR/MWh_h] | 0.8 | 0.9 | 1 | 1 | 0.5 | 0.9 |  |  | 0.5 | 1
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0.3 | 0.3 | 0.5 | 0.6 | 0.1 | 0.3 |  |  | 0.1 | 0.6
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.5 |  |  | 0.3 | 0.5
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 1100 | 1070 | 1020 | 920 | 1000 | 1100 |  |  | 900 | 1000
Technology-specific data
| Startup cost [2015-EUR/MW_h/startup] | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0
Notes:
A. The investment and O&M costs are assessed in relation to an approx. operation in 500 hours/year.
B. The installation at low voltage necessitates a transformer substation & expansion of the distribution board. Costs for these are included in the stated equipment costs.
C. Electrode boilers at medium-high voltage are directly connected to the distribution grid. Costs for the distribution board are included in the equipment costs.
D. The installation costs include costs for electrical integration & grid connection fees.
E. The forced outage of electric boilers is very limited and typically well below 1 %. The planned outage is typically limited to 1 day/year.
F. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Tjæreborg Industri, 2016
2. Parat, unknown date, Brochure High Voltage Electrode Boiler, available at http://parat.no/media/201154/Electrode-Boiler-web.pdf

## 44 Natural Gas DH Only
Technology |  | Gas boiler - boiler - natural gas - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | lower: 0.5; upper: 10; lower: 0.5; upper: 10
| Heat efficiency (net, annual average) [] | 103% | 103% | 104% | 104% | 93% | 105% | 94% | 106% | B | [1, 3]
| Heat efficiency (net, name plate) [] | 105% | 105% | 106% | 106% | 95% | 107% | 96% | 108% | A | [1, 2, 3]
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.15% | 0.14% | 0.12% | 0.1% | 0.13% | 0.2% | 0.08% | 0.15% | L | 1
| Forced outage [] | 1% | 1% | 1% | 1% | 0.08% | 2% | 0.08% | 2% |  | 3
| Planned outage [weeks per year] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.6 | 0.3 | 0.6 | F | 3
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 |  | 25 |  | K | 3
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 0.7 | 0.2 | 0.7 | F | 9
| Space requirement [1000 m2/MW_h] | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.01 | E | 2
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 15% | 15% | 15% | 15% | 10% | 20% | 10% | 20% |  | 9
| Warm start-up time [hours] | 0.1 | 0.1 | 0.1 | 0.1 | 0.08 | 0.15 | 0.08 | 0.15 | D | 9
| Cold start-up time [hours] | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.5 | 0.3 | 0.5 | D | 9
Environment
| SO2 [g/GJ_i] | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0.3 | 0 | 0.3 | H | 1
| NOX [g/GJ_i] | 10 | 9 | 7 | 6 | 8 | 60 | 5 | 30 |  | [1, 2]
| CH4 [g/GJ_i] | 3 | 3 | 2 | 2 | 2 | 6 | 2 | 6 |  | [1, 2]
| N2O [g/GJ_i] | 1 | 1 | 1 | 1 |  |  |  |  | I | 7
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.06 | 0.06 | 0.05 | 0.05 | 0.04 | 0.25 | 0.04 | 0.25 | J | [2, 3]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.04 | 0.04 | 0.03 | 0.03 | 0.03 | 0.15 | 0.03 | 0.15 |  | [2, 3]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.1 | 0.01 | 0.1 |  | [2, 3]
| Variable O&M (*total) [2015-EUR/MWh_h] | 1.1 | 1.1 | 1 | 1 | 0.6 | 2.1 | 0.6 | 2.2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | L
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 1 | 1 | 0.9 | 0.9 | 0.5 | 2 | 0.5 | 2 |  | [8, 9]
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 2000 | 1950 | 1900 | 1700 | 1000 | 2500 | 1000 | 2500 | F
Notes:
A. Includes a condensing economizer, without economizer the efficiency will be up to some 93-97 %, LHV reference
B. Includes a condensing economizer, without economizer the efficiency will be up to some 92-95 %, LHV reference
C. Not Relevant for heat-only technologies
D. Boilers with low water content (e.g. watertube instaed of shell tube 3-5 pass boilers) are used start up time from cold is shorter
E. Boilers in the low power range approx. 0.010 and boilersin the higher power range 0.003
F. DGC Estimate
G. Ultra Low NOx burners can reach a level of 5 g/GJ
H. Fuel dependent , not tecchnology dependent
I. No data available
J. The average numbers are for a 2- 3 MW boiler installation
K. Technical lifetime often exceeds 25 years
L. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. DGC efficiency and emission test reports from district heating boilers, 2014
2. Burner and boiler manufacturer informations, 2015
3. Danish District Heating Association, data from a 2012 survey for the report
7. National Environmental Research Institute, Denmark 2009
8. Elsam/Elkraft update "Teknologidata for el- og varmeproduktionsanlæg", 1997
9. DGC calculations, estimates

## 45.1.a Geothermal DH, 1200m, E
Technology |  | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 11.42 | 11.37 | 11.33 | 11.24 | 11.2 | 19.28 | 4.28 | 19.28 | 4.28 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 460.3% | 467.2% | 474% | 487.6% | 494.2% | 530.9% | 405.9% | 575.5% | 431.6% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 4.121% | 4.138% | 4.154% | 4.185% | 4.199% | 1.647% | 7.423% | 1.647% | 7.423% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 2.71 | 2.65 | 2.5 | 2.44 | 2.38 | 1.63 | 4.06 | 1.52 | 3.76 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 1.54 | 1.49 | 1.45 | 1.4 | 1.36 | 0.86 | 2.31 | 0.78 | 2.1 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.67 | 0.67 | 0.57 | 0.57 | 0.57 | 0.47 | 0.95 | 0.47 | 0.93 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.51 | 0.5 | 0.48 | 0.47 | 0.45 | 0.3 | 0.79 | 0.27 | 0.72 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 5.7 | 5.71 | 6.13 | 6.25 | 5.86 | 5.09 | 6.09 | 5.75 | 6.64 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 5.7 | 5.71 | 6.13 | 6.25 | 5.86 | 5.09 | 6.09 | 5.75 | 6.64 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 22600 | 21900 | 21300 | 20600 | 19900 | 21900 | 21900 | 19900 | 19900 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 568% | 579.1% | 590.3% | 612.5% | 623.7% | 579.1% | 579.1% | 623.7% | 623.7% | [A, N]
| Heat generation from heat pumps [MW_h] | 2.01 | 1.96 | 1.92 | 1.84 | 1.8 | 3.31 | 0.74 | 3.03 | 0.67 | A | 1
| Heat generation from geothermal ressource [MW_h] | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.53 | 15.88 | 3.53 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
Notes:
A. No part of the geothermal heat is transferred directly to DH water, all is used as source for the heat pump Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1800 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.1.b Geothermal DH, 2000m, E
Technology |  | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 13.14 | 13.11 | 13.09 | 13.05 | 13.03 | 22.18 | 4.93 | 22.18 | 4.93 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 844.4% | 855.3% | 866.1% | 887% | 897.2% | 1124% | 650.4% | 1208% | 677.4% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 6.501% | 6.513% | 6.523% | 6.543% | 6.553% | 3.712% | 9.27% | 3.712% | 9.27% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 2.88 | 2.8 | 2.69 | 2.61 | 2.53 | 1.7 | 4.14 | 1.56 | 3.79 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 1.98 | 1.92 | 1.86 | 1.81 | 1.75 | 1.14 | 2.83 | 1.03 | 2.57 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.24 | 0.24 | 0.21 | 0.21 | 0.2 | 0.17 | 0.34 | 0.17 | 0.34 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.66 | 0.64 | 0.62 | 0.6 | 0.58 | 0.39 | 0.97 | 0.36 | 0.88 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 4.59 | 4.52 | 4.59 | 4.56 | 4.34 | 4.29 | 4.65 | 4.31 | 4.62 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 4.59 | 4.52 | 4.59 | 4.56 | 4.34 | 4.29 | 4.65 | 4.31 | 4.62 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 23900 | 23200 | 22500 | 21800 | 21100 | 23200 | 23200 | 21100 | 21100 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | L | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 505% | 514.9% | 524.8% | 544.6% | 554.5% | 514.9% | 514.9% | 554.5% | 554.5% | [A, N]
| Heat generation from heat pumps [MW_h] | 0.95 | 0.92 | 0.9 | 0.86 | 0.84 | 1.56 | 0.35 | 1.43 | 0.32 | A | 1
| Heat generation from geothermal ressource [MW_h] | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.58 | 4.57 | 20.58 | 4.57 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 68% of geothermal heat can be exchanged directly, leaving 32 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 2000 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 68/33 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.2.a Geothermal DH, 1200m, A
Technology |  | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 22.66 | 22.47 | 22.3 | 22.12 | 21.95 | 38.56 | 8.56 | 38.56 | 8.56 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 165.1% | 166% | 166.9% | 167.8% | 168.7% | 172.3% | 164.4% | 179.4% | 170.9% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 2.076% | 2.093% | 2.11% | 2.127% | 2.143% | 0.8237% | 3.701% | 0.8237% | 3.701% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 1.26 | 1.23 | 1.19 | 1.15 | 1.12 | 0.74 | 1.88 | 0.69 | 1.74 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.77 | 0.75 | 0.73 | 0.71 | 0.68 | 0.43 | 1.16 | 0.39 | 1.05 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.23 | 0.22 | 0.22 | 0.21 | 0.2 | 0.16 | 0.33 | 0.16 | 0.33 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.26 | 0.25 | 0.24 | 0.24 | 0.23 | 0.15 | 0.4 | 0.13 | 0.36 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.08 | 2.11 | 2.14 | 2.13 | 2.11 | 2.07 | 2.07 | 2.03 | 2.03 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 2.08 | 2.11 | 2.14 | 2.13 | 2.11 | 2.07 | 2.07 | 2.03 | 2.03 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 11100 | 10800 | 10500 | 10100 | 9800 | 10800 | 10800 | 9800 | 9800 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 171% | 172% | 173% | 174% | 175% | 172% | 172% | 175% | 175% | [A, N]
| Heat generation from heat pumps [MW_h] | 13.25 | 13.07 | 12.89 | 12.71 | 12.54 | 22.06 | 4.89 | 21.17 | 4.69 | A | 1
| Heat generation from geothermal ressource [MW_h] | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.52 | 15.88 | 3.52 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
Notes:
A. No part of the geothermal heat is transferred directly to DH water. 100% heat source for the heat pump. Heat pump according to Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1800 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.2.b Geothermal DH, 2000m, A
Technology |  | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 17.58 | 17.51 | 17.44 | 17.37 | 17.3 | 29.84 | 6.62 | 29.84 | 6.62 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 292.9% | 295.3% | 297.7% | 300.1% | 302.6% | 316.9% | 274.8% | 329.5% | 284.2% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 4.857% | 4.877% | 4.898% | 4.918% | 4.937% | 2.761% | 6.903% | 2.761% | 6.903% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 2.09 | 2.03 | 1.97 | 1.91 | 1.85 | 1.26 | 2.87 | 1.14 | 2.6 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 1.48 | 1.44 | 1.39 | 1.35 | 1.31 | 0.82 | 2.11 | 0.74 | 1.91 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.12 | 0.12 | 0.11 | 0.11 | 0.11 | 0.16 | 0.04 | 0.14 | 0.03 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.49 | 0.48 | 0.46 | 0.45 | 0.44 | 0.28 | 0.72 | 0.26 | 0.66 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 2.99 | 2.96 | 2.92 | 2.86 | 2.8 | 2.93 | 2.93 | 2.74 | 2.74 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 2.99 | 2.96 | 2.92 | 2.86 | 2.8 | 2.93 | 2.93 | 2.74 | 2.74 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 17300 | 16800 | 16300 | 15800 | 15300 | 16800 | 16800 | 15300 | 15300 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 171% | 172% | 173% | 174% | 175% | 172% | 172% | 175% | 175% | [A, N]
| Heat generation from heat pumps [MW_h] | 5.39 | 5.32 | 5.25 | 5.18 | 5.11 | 9.01 | 2 | 8.65 | 1.92 | A | 1
| Heat generation from geothermal ressource [MW_h] | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.6 | 4.57 | 20.6 | 4.57 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 68% of geothermal heat can be exchanged directly, leaving 32 as heat source for the heat pump. Heat pump according to Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 68/33 (°C source/return). Temperature of DH water is 80/40 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.3.a Geoth. DH, 1200m, E (LT)
Technology |  | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 10.93 | 10.9 | 10.86 | 10.8 | 10.77 | 18.45 | 4.1 | 18.45 | 4.1 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 548.1% | 556.1% | 564% | 579.6% | 587.3% | 651.7% | 467.8% | 704.3% | 494.3% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 4.304% | 4.318% | 4.331% | 4.356% | 4.368% | 1.721% | 7.749% | 1.721% | 7.749% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 2.7 | 2.64 | 2.49 | 2.43 | 2.37 | 1.6 | 4.04 | 1.48 | 3.74 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 1.6 | 1.56 | 1.51 | 1.46 | 1.42 | 0.89 | 2.41 | 0.81 | 2.2 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.56 | 0.56 | 0.48 | 0.48 | 0.48 | 0.4 | 0.8 | 0.39 | 0.79 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.53 | 0.52 | 0.5 | 0.49 | 0.47 | 0.31 | 0.83 | 0.28 | 0.75 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 5.46 | 5.45 | 5.78 | 5.86 | 5.51 | 4.93 | 5.77 | 5.43 | 6.18 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 5.46 | 5.45 | 5.78 | 5.86 | 5.51 | 4.93 | 5.77 | 5.43 | 6.18 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 23200 | 22500 | 21800 | 21100 | 20500 | 22500 | 22500 | 20500 | 20500 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 603% | 614.8% | 626.6% | 650.3% | 662.1% | 614.8% | 614.8% | 662.1% | 662.1% | [A, N]
| Heat generation from heat pumps [MW_h] | 1.52 | 1.49 | 1.46 | 1.39 | 1.36 | 2.51 | 0.56 | 2.3 | 0.51 | A | 1
| Heat generation from geothermal ressource [MW_h] | 9.41 | 9.41 | 9.41 | 9.41 | 9.41 | 15.88 | 3.53 | 15.88 | 3.53 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 19% of geothermal heat can be exchanged directly, leaving 79 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 44/17 (°C source/return). Temperature of DH water is 70/35 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.3.b Geoth DH, 2000m, E (LT)
Technology |  | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 12.65 | 12.64 | 12.63 | 12.61 | 12.6 | 21.35 | 4.73 | 21.35 | 4.73 | [I, A] | [1, 2]
| Heat efficiency (net, annual average) [] | 1185% | 1196% | 1207% | 1228% | 1237% | 1830% | 816.9% | 1937% | 837.6% | AG
| Auxiliary Electricity consumption (share of heat gen.) [] | 6.75% | 6.755% | 6.761% | 6.771% | 6.776% | 3.856% | 9.662% | 3.856% | 9.662% | B | [2, 3, 4]
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) [] | bar: note
Secondary regulation (of full load, per minute) [] | bar: note
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | [2, 5]
Warm start-up time [hours]
| Cold start-up time [hours] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 2.88 | 2.79 | 2.69 | 2.61 | 2.53 | 1.63 | 4.15 | 1.49 | 3.79 | [C, K] | [2, 4, 7]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 2.06 | 2 | 1.94 | 1.87 | 1.81 | 1.14 | 2.95 | 1.04 | 2.68 |  | [2, 4]
| Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | 0.13 | 0.13 | 0.11 | 0.11 | 0.11 | 0.1 | 0.19 | 0.09 | 0.19 | [J, K]
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.69 | 0.67 | 0.65 | 0.62 | 0.6 | 0.39 | 1.01 | 0.36 | 0.92 |  | [2, 4]
| Variable O&M (*total) [2015-EUR/MWh_h] | 4.34 | 4.25 | 4.24 | 4.16 | 3.99 | 4.12 | 4.33 | 3.98 | 4.16 | FJ | 2
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 4.34 | 4.25 | 4.24 | 4.16 | 3.99 | 4.12 | 4.33 | 3.98 | 4.16 | F
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 24500 | 23800 | 23100 | 22300 | 21600 | 23800 | 23800 | 21600 | 21600 | [E, J] | [1, 3, 2]
Technology-specific data
| Number of injection wells | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 3 | 2 | [L, N] | 1
| Number of production wells | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 3 | 1 | [L, N] | 1
| Heat pump SCOP (net, annual average) [] | 557% | 567.9% | 578.8% | 600.7% | 611.6% | 567.9% | 567.9% | 611.6% | 611.6% | [A, N]
| Heat generation from heat pumps [MW_h] | 0.46 | 0.45 | 0.44 | 0.42 | 0.41 | 0.76 | 0.17 | 0.69 | 0.15 | A | 1
| Heat generation from geothermal ressource [MW_h] | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 20.58 | 4.57 | 20.58 | 4.57 | [I, A, L, N] | 1
| Depth of geothermal well [m] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump, 83% of geothermal heat can be exchanged directly, leaving 17 as heat source for the heat pump. Heat pump COP calculated according to [15] with Lorentz efficiency 0,5. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey, and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 1900 EUR/m is assumed.
D. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary.
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Include maintenance of filters and wells (chemical treatment)
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electric heat pumps may provide some of regulation though, e.g. in connection with a heat storage
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Including heat pump nominal investment and O&M costs - re.datasheets in chapter 40 Heat pumps
K. The base for the specific investment is the heat generation capacity for one unit including heat pumps.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 80/40 (°C source/return). Temperature of DH water is 70/35 (°C source/return)
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Data collected from European energy projects
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 45.4 Geothermal DH, E lar scale
Technology |  | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large
year |  | 2020 | 2025 | 2030 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_h] | 121 | 120.77 | 120.38 | 119.67 | 119.32 | 120.77 | 120.77 | 119.32 | 119.32 | I,A | 1, 2
| Heat efficiency (net, annual average) [] | 374% | 374% | 374% | 378.2% | 385.3% | 374% | 374% | 385.3% | 385.3% | A,G
Heat efficiency (net, name plate) []
| Auxiliary Electricity consumption (share of heat gen.) [] | 9.626% | 9.626% | 9.626% | 9.5% | 9.4% | 9.626% | 9.626% | 9.626% | 9.4% | B | 2, 3; 4
| Forced outage [] | 2% | 2% | 2% | 2% | 2% | 1% | 3% | 1% | 3% |  | 5
| Planned outage [weeks per year] | 2 | 2 | 2 | 2 | 2 | 1 | 4 | 1 | 4 |  | 5
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 30 | 25 | 35 |  | 5
| Construction time [years] | 4.5 | 4.5 | 4 | 4 | 4 | 4 | 5 | 3 | 5 |  | 5
| Space requirement [1000 m2/MW_h] | 5 | 5 | 5 | 5 | 5 | 3 | 7 | 3 | 7 | D | 5
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
| Minimum load (of full load) [] | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | H | 2; 5
| Warm start-up time [hours] | 4 | 4 | 4 | 4 | 4 | 3 | 5 | 3 | 5
| Cold start-up time [hours] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 3
Environment
SO2 (degree of desulphuring) []
NOX [g/GJ_i]
CH4 [g/GJ_i]
N2O [g/GJ_i]
Particles [g/GJ_i]
Financial data
| Nominal investment (*total) [2020-MEUR/MW_h] | 1.34 | 1.3 | 1.27 | 1.23 | 1.2 | 1.11 | 1.5 | 1.02 | 1.38 | C,K | 2, 4, 7
| Nominal investment (heatpump, installation incl) [2020-MEUR/MW_h] | 0.27 | 0.26 | 0.25 | 0.25 | 0.24 | 0.22 | 0.3 | 0.2 | 0.28 | J | 2, 4
| Nominal investment (surface installation excl. heatpump) [2020-MEUR/MW_h] | 0.4 | 0.39 | 0.38 | 0.37 | 0.36 | 0.33 | 0.45 | 0.31 | 0.41 | J
| Nominal investment (wells and down hole eq.) [2020-MEUR/MW_h] | 0.67 | 0.65 | 0.63 | 0.62 | 0.6 | 0.55 | 0.75 | 0.51 | 0.69 |  | 2, 4
| Variable O&M (*total) [2020-EUR/MWh_h] | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | F,J | 2, 4
| Variable O&M (electricity cost) [2020-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | M
| Variable O&M (other O&M) [2020-EUR/MWh_h] | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 2.02 | 3 | 2.02 | 3 | F | 2, 4
| Fixed O&M (*total) [2020-EUR/MW_h/y] | 18791.95 | 18255.03 | 17718.12 | 17104.51 | 16567.59 | 15516.78 | 20993.29 | 14082.45 | 19052.73 | E,J | 2, 4
Startup cost [2020-EUR/MW_h/startup]
Technology-specific data
| Nominal Abandonment Cost (ABEX) [2020-MEUR/MW_h] | 0.1 | 0.1 | 0.1 | 0.09 | 0.09 | 0.08 | 0.11 | 0.08 | 0.1 | O | 2, 7
| Number of injection wells | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | L, N | 2
| Number of production wells | 6 | 6 | 6 | 6 | 6 | 6 | 12 | 6 | 12 | L | 2
| Heat pump SCOP (net, annual average) [] | 377% | 381.2% | 388.4% | 402.5% | 409.7% | 381% | 381% | 410% | 410% | A, N
| Heat generation from heat pumps [MW_h] | 21 | 20.77 | 20.38 | 19.67 | 19.32 | 17.65 | 23.88 | 16.43 | 22.22 | A | 2
| Heat generation from geothermal ressource [MW_h] | 100 | 100 | 100 | 100 | 100 | 85 | 115 | 85 | 115 | I,A,L,N | 2
| Depth of geothermal well [m] | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |  | 1, 2
Notes:
A. Part of the geothermal heat is transferred directly to DH water. In combination with an electric heat pump. 44% of geothermal heat can be exchanged directly, leaving 56% as heat source for the heat pump. Heat pump COP based on specific case according to [2]. Improved COP as per Ch. 40.
B. The total electricity demand for submerged pumps / reinjection pumps etc. This will vary according to reservoir properties. Lower / upper case considers variations.
C. Based on large scale effects. Includes CAPEX for the heat pump. Does not include project development costs e.g. initial screening, seismic survey etc. and geological model, estimated to 1,5-3 MEUR/site (based on 1;4 and Ref. [10]). A well cost of 2000 EUR/m is assumed.
D. The requirement is per facility. This will vary with the design. Requirements are usually higher during construction phase. In case of vertical injection wells a horizontal offset in the range of 1-2 km for the injection wells is necessary
E. Replacement of submersible pump(s), approx. once every five years, operation staff. Heat pump fixed O&M included, as per see datasheets in Chapter 40 Heat pumps.
F. Including maintenance of filters and wells (chemical treatment). Does not include drilling of replacement wells.
G. Total efficiency is calculated as heat output divided by energy input. Energy input is input to heat pump and auxiliary electricity to pumps etc.
H. A geothermal plant is intended for continuous operation. Electrical heat pumps may provide some of the regulation though, e.g. in connection with an energy storage to allow for use of the heating when required.
I. Uncertainty does not consider the risk of not finding a suitable reservoir.
J. Heat pump nominal investment costs including installation and integration with geothermal plant, excl. Building integration, electrical supply and district heating connection
K. The basis of the specific investment is the heat generation capacity for one unit including heat pumps but excluding ABEX.
L. Lower / upper cases considers variations in the plant size in terms of numbers of wells.
M. Auxiliary electricity consumption is included in the total efficiency. Can be calculated separately based on the figure above.
N. Temperature of geothermal heat is 65/10 (°C source/return). Temperature of DH water is (°C source/return) 90/45 (500 h), 85/40 (1500 h) and 80/40 (rest of estimated hours)
O. Abandonment Cost (ABEX) accounts for approx. 7,5 % of total nominal investment [2]
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. PlanEnergi, GEUS, 2019
2. Input from Innargi Nov 2021 - One case scenario
3. Thisted District Heating, Personal Communication
4. Energy Technology Data Catalogue, June 2019
5. European Technology platform on Renewable Heating and Cooling, 2014, Geothermal Technology Roadmap
6. Technology Catalogue, Ch. 40 (2020)
7. Input from APMH March 2020 (drilling costs variations with depth)

## 46 Solar District Heating
Technology |  | Solar DH - renewable heat - solar - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Heat efficiency (net, annual average) [] | 43% | 45% | 48% | 49.95% | 42% | 49% | 46% | 54% | P
| Auxiliary Electricity consumption (share of heat gen.) [] | 0.3% | 0.3% | 0.3% | 0.3% | 0.2% | 0.4% | 0.2% | 0.4%
| Forced outage [] | 0.5% | 0.5% | 0.5% | 0.5% | 0% | 1% | 0% | 1% | K
| Technical lifetime [years] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | I | 17
| Construction time [years] | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Space requirement [1000 m2/MWh_h/y] | 6.7 | 6.3 | 6 | 5.7 | 6 | 6.7 | 5.5 | 6 | J
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Minimum load (of full load) [] | bar: note
Warm start-up time [hours]
Cold start-up time [hours]
Environment
| SO2 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NOX [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CH4 [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| N2O [g/GJ_i] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Financial data
| Nominal investment (*total) [2015-MEUR/MW_h] | 0.31 | 0.31 | 0.3 | 0.28 | 0.29 | 0.32 | 0.26 | 0.31 | [C, E, H, N, S] | [16, 18]
| Nominal investment (equipment) [2015-MEUR/MW_h] | 0.23 | 0.23 | 0.22 | 0.21 | 0.22 | 0.23 | 0.19 | 0.22 | O
| Nominal investment (installation) [2015-MEUR/MW_h] | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.04 | O
| Nominal investment (diurnal heat storage) [2015-MEUR/MW_h] | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.05 | 0.03 | 0.05 | [D, M]
| Variable O&M (*total) [2015-EUR/MWh_h] | 0.19 | 0.21 | 0.3 | 0.35 | 0.14 | 0.28 | 0.23 | 0.47
| Variable O&M (electricity cost) [2015-EUR/MWh_h] | 0.19 | 0.21 | 0.3 | 0.35 | 0.14 | 0.28 | 0.23 | 0.47 | R
| Variable O&M (other O&M) [2015-EUR/MWh_h] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M (*total) [2015-EUR/MW_h/y] | 57.86 | 60.81 | 56.81 | 59.71 | 56.68 | 64.29 | 54.78 | 56.81 | B
Technology-specific data
| Nominal investment (diurnal heat storage) [2015-EUR/MWh_h/y] | 60 | 57 | 54 | 52 | 41 | 75 | 37 | 68 | [D, M]
| Nominal investment (total solar system excl diurnal heat storage) [2015-EUR/MWh_h/y] | 428.89 | 395.39 | 362.11 | 325.4 | 371.04 | 422.22 | 292.08 | 362.11 | [C, H, N]
| Nominal investment (total solar system excl diurnal heat storage, per collector area) [2015-EUR/m2] | 193 | 187 | 180 | 170 | 184 | 190 | 160 | 180 | [G, H, N] | 16
| Fixed O&M (*total, per annual output) [2015-EUR/MWh_h/y] | 0.09 | 0.09 | 0.08 | 0.08 | 0.08 | 0.1 | 0.07 | 0.08 | B
| Fixed O&M (*total, per collector area) [2015-EUR/m2/y] | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | B
| Typical plant size (collector area) [m2] | 10000 | 13000 | 21000 | 55000 | 10000 | 20000 | 10000 | 100000 | L
| Collector input [MWh_i/m2/y] | 1.05 | 1.05 | 1.05 | 1.05 | 1.01 | 1.08 | 1.01 | 1.08 | Q
| Collector output [MWh_h/m2/y] | 0.45 | 0.47 | 0.5 | 0.52 | 0.45 | 0.5 | 0.5 | 0.55 | A | 4
Notes:
A. The yield is weather dependent and very site-specific, depending much on the temperatures of the district heating network. The quoted yield the average measured output from 40 Danish solar heating plants for 2015.
B. Estimate is 0,2 EUR/MWh heat output in 2015, excluding electricity consumption.
C. Applying the formula 250,000 EUR + 167 EUR/m2 solar panel collector for plants <50.000m2, cf. figures from Note G.
D. Including a diurnal storage is mandatory, 0.2 m3/m2 being a typical average storage size. This figure can vary, dependent on the local conditions and desired solar fraction.
E. Can be combined with seasonal storage, cf. corresponding chapter.
F. Solar thermal plants can be regulated by varying the flow of the heat transfer fluid. The regulation ability is limited by the available heat demand in the heat sink (incl. available storage capacity) and solar radiation.
G. 2015-Prices of different plant sizes (Ref. 1): {"5000":{"Price pr. m2 [eur\/m2]":216.0,"Total price [M-eur]":1.08},"10000":{"Price pr. m2 [eur\/m2]":193.33,"Total price [M-eur]":1.93},"20000":{"Price pr. m2 [eur\/m2]":180.0,"Total price [M-eur]":3.6},"50000":{"Price pr. m2 [eur\/m2]":174.67,"Total price [M-eur]":8.73},"100000":{"Price pr. m2 [eur\/m2]":170.0,"Total price [M-eur]":17.0}}
H. Prices include leveling of ground, laying of district heating pipelines in the ground inkl. 50 m of transmission pipeline to the district heating plant, heat exchanger connected to solar panel field and installed with collection tank and expansion with flanges to secondary side, control and electricity works, design and project management, start-up regulation and documentation.
I. The lifetime is minimum 25-30 years, proven in actual plants still in operation. Critical component is the teflon foil, not the material itself, but the application method. The pipes have been improved, designed for the relatively large number of temperature variations, compared to normal district heating pipelines. The fluid is well managed.
J. Space requirement is approximately 3 m2 for each m2 gross collector area. No development of this parameter is expected, since the main reason is to avoid the shadow effect. Minor optimization of the sides of the panels may be obtained, increasing the ratio of aperture/gross area. Other types of solar collectors such as vacuum and CSP (concentrated solar power) may have lower space requirement.
K. The forced outage is very small, therefore in practice close to 0 %. The modular construction makes it possible to maintain sections of the panels. Outage of critical components such as the heat exchanger is very limited.
L. The average plant size increases, but with large variations since both small plants and increasingly larger plants are installed. A 5 % annual increase of the average size is assumed. The plant size is rather dependent on the heat demand in the district heating grid, it is connected to. The collector area is, cf. international standards, stated as gross area.
M. Estimate of cost of tank storage (diurnal storage) is 135 EUR/m3. The required size of the storage differs, but a typical size is 0.1-0.3 m3 storage for each m2 of solar panels, hence a 10,000 m2 solar thermal plant requires 1-3,000 m3 of diurnal storage.
N. Considering a reduction in prices for 2015-2020 / 2020-2030 / 2030-2050 of 0.6 / 0.4 / 0.3 % p.a.
O. The division of cost elements is site- and plant specific. An indicative distribution of costs are; Solar collectors and piping (48%), heat exchanger, pumps etc. (8%), accumulation tank (11%), transmission pipeline (13%), building (2%), control, operation and startup (5%), land purchase, ground works (7%), design, permits, unforeseen (6%). Total for equipment is 85% and for installation is 15% (design, permits, unforeseen, ground works, control and start up), but including accumulation tank and a transmission pipeline.
P. Please refer to www.solvarmedata.dk for display of efficiencies of Danish solar district heating plants. Chose a plant, select "Production and efficiency" and a chart will display the efficiency - typically varying between 20 and 50%.
Q. The solar radiation on the horizontal surface.
R. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
S. The cost per output power is converted from cost per collector area via formula: Power/Area = 0.7 kWth/m2. Note this is an approximation, original figures are stated per area or MWh
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
4. Solar Heating plants in Denmark, Simon Furbo, Bengt Perers and Federico Bava, Department of Civil Engineering, Technical University of Denmark. The projected outputs for 2020, 2030 and 2050 are not from this reference.
16. Arcon-Sunmark, personal communication. The projected costs are not from this reference, but estimated based on two components; the lower specific costs of larger plants in 2015 and increased competition among suppliers and more efficient production of solar panels.
17. "Life expectancy of solar collectors in solar district heating systems", Department of Civil Engineering, Technical University of Denmark, 2009.
18. "Recommendation1: Converting solar thermal collector area into installed capacity (m2 to kWth) ", Solar Heaing and Cooling programme, IEA , 2004.

## 50 Diesel engine farm
Technology |  | Engine, peak plant - back pressure - diesel - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 18; note: [A, B]
| Electrical efficiency (net, annual average) [] | 35% | 35% | 35% | 35% | 33% | 37% |  |  | C
| Electrical efficiency (net, name plate) [] | 37% | 37% | 37% | 37% | 35% | 39% |  |  |  | [1, 2, 3]
Cb coefficient (50°C/100°C)
Cv coefficient (50°C/100°C)
| Forced outage [] | ctrl: 0.9%; ctrl: 0.9%; ctrl: 0.9%; ctrl: 0.9%; ref: 4
| Planned outage [weeks per year] | 0.17 | 0.17 | 0.17 | 0.17 |  |  |  |  | [D, E] | 5
| Technical lifetime [years] | ctrl: 25; ctrl: 25; ctrl: 25; ctrl: 25
| Construction time [years] | ctrl: 1; ctrl: 1; ctrl: 1; ctrl: 1; ref: 6
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 100% | 100% | 100% | 100% |  |  |  |  | F | 6
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% |  |  |  |  | F | 6
Minimum load (of full load) [] | bar: ctrl to ctrl; note
| Warm start-up time [hours] | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.03 |  |  | H | [6, 7]
| Cold start-up time [hours] | 0.09 | 0.09 | 0.09 | 0.09 | 0.05 | 0.17 |  |  | H | 6
Environment
| SO2 [g/GJ_i] | 23 | 23 | 23 | 23 |  |  |  |  | I | 8
| NOX [g/GJ_i] | ctrl: 942; ctrl: 942; ctrl: 942; ctrl: 942; ref: 8
| CH4 [g/GJ_i] | ctrl: 24; ctrl: 24; ctrl: 24; ctrl: 24; ref: 8
| N2O [g/GJ_i] | ctrl: 2.1; ctrl: 2.1; ctrl: 2.1; ctrl: 2.1; ref: 8
| Particles [g/GJ_i] | ctrl: 5; ctrl: 5; ctrl: 5; ctrl: 5; ref: 8
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 0.35 | 0.34 | 0.34 | 0.34 | 0.27 | 0.41 | 0.24 | 0.44 | [M, N, O] | [1, 6, 9, 10]
| Nominal investment (equipment) [2015-MEUR/MW_e] | ctrl: 0.23; ctrl: 0.22; ctrl: 0.22; ctrl: 0.22; note: L
| Nominal investment (installation) [2015-MEUR/MW_e] | ctrl: 0.12; ctrl: 0.12; ctrl: 0.12; ctrl: 0.12; note: L
| Variable O&M (*total) [2015-EUR/MWh_e] | 6 | 6 | 6 | 6 | 2.6 | 8.5 | 2.6 | 8.5 |  | [11, 12, 13]
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 8800 | 8800 | 8448 | 8096 |  |  |  |  | [D, P, Q] | 6
| Startup cost [2015-EUR/MW_e/startup] | note: R; ref: [6, 11]
Notes:
A. The range of generating capacity for a plant based on this technology is tipically 10-300 MW. Most of UK projects are in the range 18.5-20 MW. Emission requirements for plants with 18.5 MW and above are regulated by the Danish EPA and it is as of yet undetermined whether and exemption due to low operating hours can be obtained.
B. Engine size is normally in the range 400 kW - 2 MW. Here considered 10 engines of 1.8 MW.
C. Assuming the same efficiency reduction from nameplate to annual average compared to Gas Engines in the main technology catalogue.
D. The routine checks and oil change varies depending on the size. Smaller engines (400 kW) needs it every 250 h, while larger engines (2 MW) needs it every 1000h. Here assumed larger engines. Fixed O&M costs can increase for smaller sizes.
E. 1.5h monthly maintenance for general checks, 4h semiannual, 2h annually, 2h biannually, 6h every 6 years.
F. 50% of the output capacity can be reach within 15 seconds and after 20 seconds the total power output can be provided.
G. Minimum load of the single engine is 30%. In a modular solution, some engines can be switched off to reduce the minimum load of the total plant. This way the performance is maintained at the optimal level.
H. The startup time of the single engine is around 30 seconds. The syncronization of all the machines and the connection to the grid might increase the startup time to 3-10 minutes.
I. Values related to the use of gas oil.
L. Split based on the Engine technology in the main technology catalogue
M. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
N. The specific investment cost can vary depending on a number of parameters, like size of engines, electrical equipment and other engines characteristics. The specific investment in 2015 from several projects and sources is in the range 0.282-0.456 MEUR/MW.
O. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
P. Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
Q. Assumed two times the reported value for service agreement excluding consumables, to take into account other fixed O&M components.
R. The maintenance schedule is not affected by frequent starts and stops, fuel, or trips as modern combustion engines have the capability to stop and start without limitations or maintenance impact.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Interview with Rolls Royce Power Systems
2. C. Breyer. Fuel-Parity: New very large and sustainable market segments for PV systems. 2010
3. National Grid. Short Term Operating Reserve - Carbon intensity report. 2016
4. EEA. Distributed Generation Operational Reliability and Availability Database. 2004
5. Maintenance schedule Caterpillar Emergency generator. Available at: https://ae.usembassy.gov/wp-content/uploads/sites/254/2017/06/stc12017q0002_post-provided-generator-checklist.pdf
6. Interview with UK manufacturer: Edina Power UK
7. Warstsila. White paper - Combustion engine power plants. 2011
8. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
9. Timera Energy. Investment in UK peaking assets. Available at: www.timera-energy.com/investment-in-uk-peaking-assets
10. UK Department for Business, Energy and Industrial Strategy. Electricity Generation Cost. November 2016
11. EUGINE (European Engine Power Plants Association) questionnaire to their members. Data presented in "Flexibility Needs and Options for Europe's Future Electricity System", Energy Brainpool, September 2017.
12. BEIS. Electricity Generation cost. November 2016
13. LAZARD. Levelized cost of energy analysis v11. November 2017

## 51 Natural gas engine plant
Technology |  | Engine, peak plant - back pressure - natural gas - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 200; ctrl: 200; ctrl: 200; ctrl: 200; note: [A, B]
| Electrical efficiency (net, annual average) [] | 46% | 46% | 48% | 48% |  |  |  |  | D | 2
| Electrical efficiency (net, name plate) [] | 48% | 48% | 50% | 50% |  |  |  |  | C | 1
Cb coefficient (50°C/100°C)
Cv coefficient (50°C/100°C)
| Forced outage [] | ctrl: 0.9%; ctrl: 0.9%; ctrl: 0.9%; ctrl: 0.9%; ref: 3
| Planned outage [weeks per year] | ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; ctrl: 0.03; note: E
| Technical lifetime [years] | ctrl: 25; ctrl: 25; ctrl: 25; ctrl: 25; note: F
| Construction time [years] | ctrl: 1; ctrl: 1; ctrl: 1; ctrl: 1; ref: [4, 5]
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 60% | 60% | 60% | 60% |  |  |  |  | G | 6
| Secondary regulation (of full load, per minute) [] | 100% | 100% | 100% | 100% |  |  |  |  | G | 6
| Minimum load (of full load) [] | 1.5% | 1.5% | 1.5% | 1.5% |  |  |  |  | H | [6, 7]
| Warm start-up time [hours] | 0.03 | 0.03 | 0.03 | 0.03 |  |  |  |  | I | 7
| Cold start-up time [hours] | 0.17 | 0.17 | 0.17 | 0.17 |  |  |  |  | I | 7
Environment
| SO2 [g/GJ_i] | 0 | 0 | 0 | 0 |  |  |  |  | F | 2
| NOX [g/GJ_i] | 75 | 75 | 75 | 75 |  |  |  |  | F | 2
| CH4 [g/GJ_i] | 315 | 315 | 315 | 315 |  |  |  |  | F | 2
| N2O [g/GJ_i] | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  |  | F | 2
| Particles [g/GJ_i] | ctrl: 0.76; ctrl: 0.76; ctrl: 0.76; ctrl: 0.76; ref: 8
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 0.51 | 0.49 | 0.47 | 0.45 | 0.4 | 0.59 | 0.31 | 0.58 | [L, M, N, R] | [7, 5, 9]
| Nominal investment (equipment) [2015-MEUR/MW_e] | 0.33 | 0.32 | 0.31 | 0.29 |  |  |  |  | F | 2
| Nominal investment (installation) [2015-MEUR/MW_e] | 0.18 | 0.17 | 0.17 | 0.16 |  |  |  |  | F | 2
| Variable O&M (*total) [2015-EUR/MWh_e] | 6 | 6 | 6 | 6 | 2.6 | 8.5 | 2.6 | 8.5 |  | [10, 11, 12]
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 6500 | 6500 | 6250 | 6000 |  |  |  |  | [O, P] | 7
| Startup cost [2015-EUR/MW_e/startup] | 0 | 0 | 0 | 0 |  |  |  |  | Q | 10
Notes:
A. The technology is modular, normally composed by a certain amount of 2-10 MW engines. Here 20 engines of 10 MW are considered.
B. Typical capacity for ultra peakers and emergency plants is in the range 20-300 MW
C. Based on large gas motor (Wartsila 34SG)
D. Assuming the same efficiency reduction from nameplate to annual average compared to main technology catalogue.
E. Based on maintenance schedule of gas engines, considering the reduced number of operating hours and the fact that a typical scheduled maintenance services occurs after 2000, 4000 and 6000 hours, with 1 or 2 days of downtime each. No major maintenance window (16,000 h) is reached.
F. Based on the Gas Engine in the main technology catalogue
G. The values refers to the engine at nominal operating temperature.
H. Minimum load of the single engine is 30%. In a modular solution, some engines can be switched off to reduce the minimum load of the total plant. This way the performance is maintained at the optimal level. Calculation done assuming 20x10MW engines.
I. The engines can startup from warm in 2 minutes. The plant cold startup time is affected by the need to warm up the transformers, which brings it up to 10 minutes. If engines and transformers are hot, the startup time is lower. In case of smaller plants connected to distribution grid, the time to warm up the transformer might not constitute a bottleneck.
L. Dual fuel operation can be considered. Impacting 3-4% of the total plant cost and 7% of engine cost
M. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
N. The specific investment cost can vary depending on a number of parameters, like size of engines, electrical equipment and other engines characteristics. The specific investment in 2015 from several projects and sources is in the range 0.443-0.616 MEUR/MW. The lower bound refers to smaller plants with smaller engines, while the higher bound refers to dual fuel plant, located further away from the grid.
O. The fixed O&M cost is lower than a typical value for plants operating >4000 h a year. A typical large maintenance window including reinvestment is carried after 10,000 running hours. Due to the low utilization, this type of plants might never need it in its lifetime, reducing the fixed O&M cost drastically. Additionally the central and lower estimates assume unmanned/remote operation of the plant, whereas the upper boundary assumes manned operation.
P. Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
Q. The maintenance schedule is not affected by frequent starts and stops, fuel, or trips as modern combustion engines have the capability to stop and start without limitations or maintenance impact. Modern technology can sustain up to 1000 cycles/years with no significant wear.
R. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. Wartsila. Power Plant solutions 2016
2. Main technology catalogue: Technology Data for Energy Plants - August 2016
3. EEA. Distributed Generation Operational Reliability and Availability Database. 2004
4. Kiisa Power plant project for Elering
5. Warstsila. White paper - Combustion engine power plants. 2011
6. D. Santoianni. Defining true flexibility - a comparison of gas-fired power generating technologies. 2015
7. Phone interview with Wartsila
8. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
9. UK Department for Business, Energy and Industrial Strategy. Electricity Generation Cost. November 2016
10. EUGINE (European Engine Power Plants Association) questionnaire to their members. Data presented in "Flexibility Needs and Options for Europe's Future Electricity System", Energy Brainpool, September 2017.
11. BEIS. Electricity Generation cost. November 2016
12. LAZARD. Levelized cost of energy analysis v11. November 2017

## 52 OCGT - Natural gas
Technology |  | Gas turbine, open cycle - back pressure - natural gas - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
| Generating capacity for one unit [MW_e] | ctrl: 100; ctrl: 100; ctrl: 100; ctrl: 100; note: A
| Electrical efficiency (net, annual average) [] | 39% | 40% | 41% | 43% |  |  |  |  | C | 3
| Electrical efficiency (net, name plate) [] | 41% | 42% | 43% | 45% |  |  |  |  | [B, C] | [1, 2]
Cb coefficient (50°C/100°C)
Cv coefficient (50°C/100°C)
| Forced outage [] | ctrl: 1.37%; ctrl: 1.37%; ctrl: 1.37%; ctrl: 1.37%; ref: 4
| Planned outage [weeks per year] | 0.11 | 0.11 | 0.11 | 0.11 |  |  |  |  | D | 1
| Technical lifetime [years] | 25 | 25 | 25 | 25 |  |  |  |  | E | 3
| Construction time [years] | 0.2 | 0.2 | 0.2 | 0.2 |  |  |  |  | F | 5
Regulation ability
| Primary regulation (of full load, per 30 seconds) [] | 30% | 30% | 30% | 30% |  |  |  |  | G | 5
| Secondary regulation (of full load, per minute) [] | 30% | 30% | 30% | 30% | 15% | 50% |  |  | H | [5, 6, 7]
| Minimum load (of full load) [] | 25% | 20% | 20% | 20% |  |  |  |  | I | 8
| Warm start-up time [hours] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.11 |  |  |  | [8, 9, 10]
| Cold start-up time [hours] | 0.17 | 0.17 | 0.17 | 0.17 | 0.12 | 0.19 |  |  | L | [1, 6, 8]
Environment
| SO2 [g/GJ_i] | ctrl: 0.43; ctrl: 0.43; ctrl: 0.43; ctrl: 0.43; ref: 11
| NOX [g/GJ_i] | ctrl: 48; ctrl: 48; ctrl: 48; ctrl: 48; ref: 11
| CH4 [g/GJ_i] | ctrl: 1.7; ctrl: 1.7; ctrl: 1.7; ctrl: 1.7; ref: 11
| N2O [g/GJ_i] | ctrl: 1; ctrl: 1; ctrl: 1; ctrl: 1; ref: 11
| Particles [g/GJ_i] | ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ref: 11
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 0.47 | 0.45 | 0.44 | 0.41 | 0.36 | 0.54 | 0.29 | 0.54 | [M, N, O] | [7, 9, 10]
| Nominal investment (equipment) [2015-MEUR/MW_e] | ctrl: 0.37; ctrl: 0.35; ctrl: 0.34; ctrl: 0.32; ref: 12
| Nominal investment (installation) [2015-MEUR/MW_e] | ctrl: 0.1; ctrl: 0.1; ctrl: 0.1; ctrl: 0.09; ref: 12
| Variable O&M (*total) [2015-EUR/MWh_e] | 4.5 | 4.5 | 4.5 | 4.5 | 3.5 | 5 | 3.5 | 5 |  | [5, 9, 10]
| Fixed O&M (*total) [2015-EUR/MW_e/y] | 8068 | 8068 | 7745.28 | 7422.56 |  |  |  |  | P | 9
| Startup cost [2015-EUR/MW_e/startup] | ctrl: 43; ctrl: 43; ctrl: 43; ctrl: 43; ref: 9
Notes:
A. The range of generating capacity for a power plant based on this technology is tipically 50-200 MW. Large aeroderivative gas turbines have a rating of 20-100 MW.
B. The efficiency is drastically reduced at part-load. The difference between efficiency at full load and part load is on average 15%.
C. Based on the Simple Cycle Turbine in the main technology catalogue. No improvement assumed in the future
D. Considering one service per year for borescope inspection (18h). No major maintenance intervals reached, due to low utilization.
E. Lifetime most likely >25years, given low utilization
F. Some manufacturers offers pre-assembled mobile packages with installation in 30 days.
G. Based on a droop control of 0.65 MW/s of a Industrial Trent 60 (66MW) turbine at self-sustained speed.
H. Based on a gas turbine at self-sustained speed. Ramp rates of 15 MW/min to 50 MW/min.
I. The minimum emissions-compliant load is around 50%, but in case emission regulations do not apply, this can be lower. The efficiency is reduced at part-load (roughly 15%)
L. The lower bound of 7 minutes might be increased to 10 minutes if the plant is connected to high voltage and transformer needs to warm up before starting operations, similarly to Natural gas engine plants.
M. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016.
N. The specific investment cost can vary depending on a number of parameters, like size of turbine, electrical equipment and other characteristics. The specific investment in 2015 from several projects is in the range 0.400-0.570.
O. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
P. Assumed a reduction of 4% in 2030 and 8% in 2050, due to automation of the power plant control and improvement in the operation
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
1. GE - Aeroderivative turbines product brochures.
2. Siemens - Aeroderivative turbine brochures
3. Main technology catalogue: Technology Data for Energy Plants - August 2016
4. EEA. Distributed Generation Operational Reliability and Availability Database. 2004
5. M. Welch, T.Krol. Flexible Power Generation for Grid Support utilizing Aero-derivative Gas Turbine Technology. 2016
6. EU Turbines. Gas and Steam Turbines Solutions for a sustainable energy mix (brochure). 2017
7. Forrsa Power plant for Fingrid. Available at: www.fingrid.fi/en/pages/news/news/2013/fingrids-new-reserve-power-plant-inaugurated-in-forssa/
8. Agora Energiwende. Flexibility in thermal power plants. 2017
9. Energy Brainpool. Flexibility Needs and Options for Europe's Future Electricity System. September 2017.
10. Phone interview with Siemens Turbomachinery UK
11. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
12. ESMAP. Technical paper: Study of Equipment Prices in the Power Sector. 2009

## 52 OCGT - Light fuel oil
Technology |  | Gas turbine, open cycle - back pressure - light fuel oil - medium
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | - | -
est |  | ctrl | ctrl | ctrl | ctrl | lower | upper | lower | upper | note | ref
cat | par
Energy/technical data
Generating capacity for one unit [MW_e]
| Electrical efficiency (net, annual average) [] | 38% | 39% | 40% | 42% | 38.5% | 40% |  |  | A | 18
| Electrical efficiency (net, name plate) [] | 4% | 41% | 42% | 44% | 40.5% | 42% |  |  | A | 18
Cb coefficient (50°C/100°C)
Cv coefficient (50°C/100°C)
Forced outage []
Planned outage [weeks per year]
Technical lifetime [years]
Construction time [years]
Regulation ability
Primary regulation (of full load, per 30 seconds) []
Secondary regulation (of full load, per minute) []
Minimum load (of full load) []
| Warm start-up time [hours] | 0.09 | 0.09 | 0.09 | 0.09 |  |  |  |  | A | 18
| Cold start-up time [hours] | 0.18 | 0.18 | 0.18 | 0.18 |  |  |  |  | A | 18
Environment
| SO2 [g/GJ_i] | 23 | 23 | 23 | 23 |  |  |  |  | B | 11
| NOX [g/GJ_i] | 230 | 230 | 230 | 230 |  |  |  |  | B | 11
| CH4 [g/GJ_i] | 3 | 3 | 3 | 3 |  |  |  |  | B | 11
| N2O [g/GJ_i] | 0.6 | 0.6 | 0.6 | 0.6 |  |  |  |  | B | 11
| Particles [g/GJ_i] | 5 | 5 | 5 | 5 |  |  |  |  | B | 11
Financial data
| Nominal investment (*total) [2015-MEUR/MW_e] | 0.39 | 0.38 | 0.36 | 0.34 | 0.3 | 0.45 | 0.24 | 0.45 | [C, D] | 19
| Nominal investment (equipment) [2015-MEUR/MW_e] | ctrl: 0.3; ctrl: 0.3; ctrl: 0.28; ctrl: 0.27; ref: 20
| Nominal investment (installation) [2015-MEUR/MW_e] | ctrl: 0.09; ctrl: 0.08; ctrl: 0.08; ctrl: 0.08; ref: 20
Variable O&M (*total) [2015-EUR/MWh_e]
Fixed O&M (*total) [2015-EUR/MW_e/y]
Startup cost [2015-EUR/MW_e/startup]
Notes:
A. Value indicate the estimated change from the correspondent value of natural gas fuelled plant (unit is the same as the paramter).
B. Emission values for Gas Oil. If Residual Oil used, SO2 emissions increased to 100g, NOx reduced to 138g and Particles to 3g.
C. Development of cost follows the assumptions explained in the introduction. 10% learning rate and capacity development based on IEA ETP 2016. Same development as natural gas fuelled plant, since the technology is the same.
D. The uncertainty is estimated based on the cost span of a number of similar observed projects. It is assumed equal to ±20% in 2020 and it increases to ±30% in 2050.
*. Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
**. The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
References:
11. Institut for Miljøvidenskab. Emission factors. Available at: http://envs.au.dk/videnudveksling/luft/emissioner/emission-factors/
18. Phone interview with Siemens Turbomachinery UK
19. Forrsa Power plant for Fingrid. Available at: www.fingrid.fi/en/pages/news/news/2013/fingrids-new-reserve-power-plant-inaugurated-in-forssa/
20. ESMAP. Technical paper: Study of Equipment Prices in the Power Sector. 2009