## Intro
Intro | Technology Data for power and heat production plants
alldata_flat
01 Coal CHP | This file contains technology data sheets related to generation of electricity and district heating. The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found.
02 LTE existing plant | Dates and descriptions of updates are listed in the ammendment sheet below.
03a Coal to wood pellets exi bo
03b Coal to wood chips n. boile | Additional information about the syntax of parameters and units in the datatabels is listed below.
03c coal to wood chips exi. boi | Parameter structure: parameter name (extra info) [unit]. For financial parameters priceyear is expressed as: [priceyear-unit]
03d coal to wood chips exi. boi | Subscript abbreviations used in the datasheets: input = _i, electricity production = _e, heat production = _h
04 Gas turb. simple cycle, L | The empty square brackets [] denote parameters expressed in terms of a proportion. The raw data is in the raw decimal form, but note that these values are formated as percentage in the wide report tables for readability.
04 Gas turb. simple cycle Sm-Me | The sheet alldata_flat contains all technology data in this catalogue in a flat format.
04 Gas turb. simple cycle Micro
05 Gas turb. CC, steam extract. | Ammendment sheet
05 Gas turb. CC, Back-pressure | Date | Sheet | Change | Notes
06 Gas engines, natural gas | 2022-06-01 | 40 Heat pumps | Addition of datasheet about CO2 heat pumps
06 Gas engines, biogas | 2022-06-01 | 45 Geothermal | Addition of datasheet about large scale geothermal with electric heat pump
08 WtE CHP, Large, 40 degree | mar-22 | 21 Offshore and near shore turbines | Offshore and Nearshore turbines updated. Financial data now in 2020€.
08 WtE CHP, Large, 50 degree | feb-22 | 22 Photovoltaics | All datasheets for PV systems updated. Financial data now in 2020€.
08 WtE CHP, Medium | apr-20 | 40 Heat pumps | Compression heat pumps (electric) updated. Datasheets now divided in 3 types and different plant sizes.
08 WtE CHP, Small | apr-20 | 45 Geothermal | Datasheets updated and now divided in 1200 m and 2000 m depth, electric- and absorption heat pumps and 2 different district heating temperatures.
08 WtE HOP | mar-20 | 09a medium and large biomass HOP | added datasheets of medium and large biomass HOP
09a Wood Chips, Large 40 degree | mar-20 | 09 Biomass plants | minor update of existing biomass datasheets
09a Wood Chips, Large 50 degree | jan-20 | 09 Biomass plants | datasheets updated
09a Wood Chips, Medium | nov-19 | 22 Photovoltaics Large | Updated data sheet for large utility scale PV systems
09a Wood Chips, Small | nov-19 | 22 Photovoltaics Tracker | New data sheet for large utility scale PV systems with single axis tracker
09b Wood Pellets, Large 40 degr | sep-19 | 21 Near shore turbines | minor adjustment
09b Wood Pellets, Large 50 degr | jun-19 | 03 Rebuilding large coal power plants to biomass | Added Datasheet d for rebuild coal fired plants to chips backpressure plant. Updated datasheets a and b for rebuild coal fired plants to wood pellets
09b Wood Pellets, Medium | maj-19 | 20 Wind turbines, on-shore | onshore and domestic turbines updated
09b Wood Pellets, Small | maj-19 | 21 Offshore and near shore turbines | offshore and nearshore tubrines updated
09c Straw, Large, 40 degree | nov-18 | 50-52 peak plants | datasheets added for diesel engine farms, natural gas engine plant and open cycle gas turbines.
09c Straw, Large, 50 degree | okt-18 | 46 Solar District Heating | update
09c Straw, Medium | mar-18 | 08 WtE plants | datasheets added
09c Straw, Small | jan-18 | 04, 05 and 06 gas turbines and engines
09a Wood Chips HOP, small | jan-18 | 11 Solid oxide fuel cell (SOFC) CHP, natural gas/biogas | datasheets added
09a Wood Chips HOP, medium | jan-18 | 12 Low temperature proton exchange membrane fuel cell (LT-PEMFC) CHP, hydrogen
09a Wood Chips HOP, large | jan-18 | 41 Electric Boiler | update
09b Wood Pellets HOP | jan-18 | 44 District heating boilers, Gas fired | update
09c Straw HOP | nov-17 | 01 Supercritical Pulverized Fuel Power Plant - Coal CHP
09a Wood Chips extract. plant
09b Wood Pellets extract. plant | Version: 12, poweranddh_2022_06_21
10 Stirling
11 SOFC-CHP
12 LT-PEMFC CHP
20 Onshore turbines
20 Domestic turbines
21 Offshore turbines
21 Near shore turbines
22 Rooftop PV residential
22 Rooftop PV commercial & industrial
22 Utility-scale ground mounted PV
22 Utility-scale ground mounted PV tracker
23 Wave Energy
40 Comp. hp, airsource 1 MW
40 Comp. hp, airsource 3 MW
40 Comp. hp, airsource 10 MW
40 Comp. hp, excess heat 1 MW
40 Comp. hp, excess heat 3 MW
40 Comp. hp, excess heat 10 MW
40 Comp. hp, seawater 20 MW
40 Absorption heat pump, DH
40 co2. hp, seawater 50-100 MW
41 Electric boiler, small
41 Electric boiler, large
44 Natural Gas DH Only
45.1.a Geothermal DH, 1200m, E
45.1.b Geothermal DH, 2000m, E
45.2.a Geothermal DH, 1200m, A
45.2.b Geothermal DH, 2000m, A
45.3.a Geoth. DH, 1200m, E (LT)
45.3.b Geoth DH, 2000m, E (LT)
45.4 Geothermal DH, E lar scale
46 Solar District Heating
50 Diesel engine farm
51 Natural gas engine plant
52 OCGT - Natural gas
52 OCGT - Light fuel oil

## alldata_flat
ws | technology | tech | type | input | size | cat | par | par_short | info | unit | priceyear | note | ref | est | year | val
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Technology-specific data | Availability [] | Availability |  | [] |  | E | 7 | ctrl | 2015 | 0.95
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Technology-specific data | Availability [] | Availability |  | [] |  | E | 7 | ctrl | 2020 | 0.95
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Technology-specific data | Availability [] | Availability |  | [] |  | E | 7 | ctrl | 2030 | 0.95
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Technology-specific data | Availability [] | Availability |  | [] |  | E | 7 | ctrl | 2050
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | A |  | ctrl | 2015 | 0.75
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | A |  | ctrl | 2020 | 0.84
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | A |  | ctrl | 2030 | 1.01
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | A |  | ctrl | 2050
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [2, 3, 3] | ctrl | 2015 | 4.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [2, 3, 3] | ctrl | 2020 | 4.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [2, 3, 3] | ctrl | 2030 | 4.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | [2, 3, 3] | ctrl | 2050
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 1 | ctrl | 2015 | 0.15
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 1 | ctrl | 2020 | 0.15
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 1 | ctrl | 2030 | 0.15
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 1 | ctrl | 2050
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | [8, 7, 9, 11] | ctrl | 2015 | 0.46
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | [8, 7, 9, 11] | ctrl | 2020 | 0.485
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | [8, 7, 9, 11] | ctrl | 2030 | 0.52
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | C | [8, 7, 9, 11] | ctrl | 2050 | 0.535
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015 | 500
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020 | 500
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030 | 500
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050 | 500
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 6 | ctrl | 2015 | 25
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 6 | ctrl | 2020 | 25
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 6 | ctrl | 2030 | 25
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 6 | ctrl | 2050 | 25
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2015 | 1.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2020 | 1.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2030 | 1.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2050 | 1.5
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2015 | 0.8
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2020 | 0.8
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2030 | 0.8
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [13, 5, 5, 5] | ctrl | 2050 | 0.8
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2015 | 38
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2020 | 35
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2030 | 35
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | B | [12, 5, 5, 5] | ctrl | 2050 | 35
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | B | 5 | ctrl | 2015 | 0.97
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | B | 5 | ctrl | 2020 | 0.97
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | B | 5 | ctrl | 2030 | 0.97
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | B | 5 | ctrl | 2050 | 0.97
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2015 | 31500
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2020 | 31000
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2030 | 30355.1176
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2050 | 29105.3196
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2015 | 1.93
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2020 | 1.9
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2030 | 1.8605
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2050 | 1.7839
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2015 | 2.95
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2020 | 2.9
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2030 | 2.8397
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2050 | 2.7228
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | [10, 14] | ctrl | 2015 | 0.18
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | [10, 14] | ctrl | 2020 | 0.15
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | [10, 14] | ctrl | 2030 | 0.15
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | [10, 14] | ctrl | 2050 | 0.1
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D | 14 | ctrl | 2015 | 0.05
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D | 14 | ctrl | 2020 | 0.05
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D | 14 | ctrl | 2030 | 0.05
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D | 14 | ctrl | 2050 | 0.05
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 14 | ctrl | 2015 | 0.04
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 14 | ctrl | 2020 | 0.04
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 14 | ctrl | 2030 | 0.04
01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 14 | ctrl | 2050 | 0.04
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 7 | ctrl | 2015 | 0.5
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 7 | ctrl | 2020 | 0.5
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 7 | lower | 2020
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 7 | upper | 2020
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 7 | ctrl | 2030 | 0.5
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [E, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [E, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [E, F] | 7 | lower | 2020 | -0.01
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [E, F] | 7 | upper | 2020 | 0.01
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [E, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [E, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [E, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [E, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [E, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [E, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [E, F] | 7 | lower | 2020 | -0.01
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [E, F] | 7 | upper | 2020 | 0.01
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [E, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [E, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [E, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [E, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | [A, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | [A, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | [A, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015 | 300
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020 | 300
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020 | 200
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020 | 400
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030 | 300
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050 | 200
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050 | 400
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | [A, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | [A, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | [A, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, F] |  | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, F] |  | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, F] |  | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, F] |  | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, F] |  | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, F] |  | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, F] |  | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, F] |  | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [4, 5, 6, 7] | ctrl | 2015 | 15
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [4, 5, 6, 7] | ctrl | 2020 | 15
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [4, 5, 6, 7] | lower | 2020
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [4, 5, 6, 7] | upper | 2020
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [4, 5, 6, 7] | ctrl | 2030 | 15
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [4, 5, 6, 7] | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [4, 5, 6, 7] | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [4, 5, 6, 7] | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | CH4 (additional to existing plant) [g/GJ_i] | CH4 | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | CH4 (additional to existing plant) [g/GJ_i] | CH4 | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | CH4 (additional to existing plant) [g/GJ_i] | CH4 | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | CH4 (additional to existing plant) [g/GJ_i] | CH4 | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | CH4 (additional to existing plant) [g/GJ_i] | CH4 | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | CH4 (additional to existing plant) [g/GJ_i] | CH4 | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | CH4 (additional to existing plant) [g/GJ_i] | CH4 | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | CH4 (additional to existing plant) [g/GJ_i] | CH4 | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | N2O (additional to existing plant) [g/GJ_i] | N2O | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | N2O (additional to existing plant) [g/GJ_i] | N2O | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | N2O (additional to existing plant) [g/GJ_i] | N2O | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | N2O (additional to existing plant) [g/GJ_i] | N2O | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | N2O (additional to existing plant) [g/GJ_i] | N2O | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | N2O (additional to existing plant) [g/GJ_i] | N2O | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | N2O (additional to existing plant) [g/GJ_i] | N2O | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | N2O (additional to existing plant) [g/GJ_i] | N2O | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | NOX (additional to existing plant) [g/GJ_i] | NOX | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | NOX (additional to existing plant) [g/GJ_i] | NOX | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | NOX (additional to existing plant) [g/GJ_i] | NOX | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | NOX (additional to existing plant) [g/GJ_i] | NOX | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | NOX (additional to existing plant) [g/GJ_i] | NOX | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | NOX (additional to existing plant) [g/GJ_i] | NOX | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | NOX (additional to existing plant) [g/GJ_i] | NOX | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | NOX (additional to existing plant) [g/GJ_i] | NOX | additional to existing plant | g/GJ_i |  | [A, F, G] | 8 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] | SO2 | degree of desulphuring, additional to existing plant | [] |  | [A, F, G] | 8 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] | SO2 | degree of desulphuring, additional to existing plant | [] |  | [A, F, G] | 8 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] | SO2 | degree of desulphuring, additional to existing plant | [] |  | [A, F, G] | 8 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] | SO2 | degree of desulphuring, additional to existing plant | [] |  | [A, F, G] | 8 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] | SO2 | degree of desulphuring, additional to existing plant | [] |  | [A, F, G] | 8 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] | SO2 | degree of desulphuring, additional to existing plant | [] |  | [A, F, G] | 8 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] | SO2 | degree of desulphuring, additional to existing plant | [] |  | [A, F, G] | 8 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Environment | SO2 (degree of desulphuring, additional to existing plant) [] | SO2 | degree of desulphuring, additional to existing plant | [] |  | [A, F, G] | 8 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2015
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2020
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | lower | 2020
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | upper | 2020
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2030
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2015
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2020
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | lower | 2020
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | upper | 2020
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2030
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | [A, B, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | [A, B, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | [A, B, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | [A, B, F] | 7 | upper | 2020 | 8000
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | [A, B, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | [A, B, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | [A, B, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | [A, B, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, F] | [4, 5, 6, 7] | ctrl | 2015 | 0.23577
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, F] | [4, 5, 6, 7] | ctrl | 2020 | 0.23577
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, F] | [4, 5, 6, 7] | lower | 2020 | 0.14825
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, F] | [4, 5, 6, 7] | upper | 2020 | 0.33693
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, F] | [4, 5, 6, 7] | ctrl | 2030 | 0.23577
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, F] | [4, 5, 6, 7] | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, F] | [4, 5, 6, 7] | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, F] | [4, 5, 6, 7] | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, D, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, D, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, D, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, D, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, D, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, D, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, D, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, D, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | [A, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | [A, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | [A, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, F] | 7 | upper | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, F] | 7 | ctrl | 2015 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, F] | 7 | ctrl | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, F] | 7 | lower | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, F] | 7 | upper | 2020 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, F] | 7 | ctrl | 2030 | 0
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, F] | 7 | ctrl | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, F] | 7 | lower | 2050
02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, F] | 7 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, C, I] | 10 | ctrl | 2015 | -0.02
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, C, I] | 10 | ctrl | 2020 | -0.02
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, C, I] | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, C, I] | 10 | upper | 2020 | -0.05
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, C, I] | 10 | ctrl | 2030 | -0.02
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, C, I] | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, C, I] | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, C, I] | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2015 | 2
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2020 | 2
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | lower | 2020 | 1.5
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | upper | 2020 | 2.5
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2030 | 2
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, C] | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, C] | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, C] | 10 | lower | 2020 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, C] | 10 | upper | 2020 | 0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, C] | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, C] | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, C] | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | [A, C] | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, C, I] | 10 | ctrl | 2015 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, C, I] | 10 | ctrl | 2020 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, C, I] | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, C, I] | 10 | upper | 2020 | -0.02
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, C, I] | 10 | ctrl | 2030 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, C, I] | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, C, I] | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, C, I] | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, C, I] | 10 | ctrl | 2015 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, C, I] | 10 | ctrl | 2020 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, C, I] | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, C, I] | 10 | upper | 2020 | -0.02
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, C, I] | 10 | ctrl | 2030 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, C, I] | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, C, I] | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, C, I] | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | lower | 2020 | -0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | upper | 2020 | 0.01
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015 | 300
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020 | 300
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020 | 200
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020 | 400
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030 | 300
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] |  | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] |  | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] |  | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] |  | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] |  | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] |  | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] |  | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] |  | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2015 | 15
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2020 | 15
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | lower | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | upper | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2030 | 15
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | lower | 2020 | 3.1
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | upper | 2020 | 3.1
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2015 | 1
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2020 | 1
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | lower | 2020 | 0.8
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | upper | 2020 | 0.8
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2030 | 1
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2015 | 20
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2020 | 21
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | lower | 2020 | 19
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | upper | 2020 | 53
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2030 | 18
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2015 | 0.3
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020 | 0.3
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030 | 0.3
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | J |  | ctrl | 2015
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | J |  | ctrl | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | J |  | lower | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | J |  | upper | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | J |  | ctrl | 2030
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | J |  | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | J |  | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | J |  | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2015
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | lower | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | upper | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2030
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2015
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | lower | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | upper | 2020
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2030
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Fixed O&M [EUR/MWe/year] | Fixed O&M |  | EUR/MWe/year |  | [A, F, K] | 10 | ctrl | 2015 | 3350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Fixed O&M [EUR/MWe/year] | Fixed O&M |  | EUR/MWe/year |  | [A, F, K] | 10 | ctrl | 2020 | 3350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Fixed O&M [EUR/MWe/year] | Fixed O&M |  | EUR/MWe/year |  | [A, F, K] | 10 | lower | 2020 | 1350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Fixed O&M [EUR/MWe/year] | Fixed O&M |  | EUR/MWe/year |  | [A, F, K] | 10 | upper | 2020 | 5350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Fixed O&M [EUR/MWe/year] | Fixed O&M |  | EUR/MWe/year |  | [A, F, K] | 10 | ctrl | 2030 | 3350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Fixed O&M [EUR/MWe/year] | Fixed O&M |  | EUR/MWe/year |  | [A, F, K] | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Fixed O&M [EUR/MWe/year] | Fixed O&M |  | EUR/MWe/year |  | [A, F, K] | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Fixed O&M [EUR/MWe/year] | Fixed O&M |  | EUR/MWe/year |  | [A, F, K] | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E, K] | [10, 11, 12] | ctrl | 2015 | 0.5
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E, K] | [10, 11, 12] | ctrl | 2020 | 0.5
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E, K] | [10, 11, 12] | lower | 2020 | 0.35
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E, K] | [10, 11, 12] | upper | 2020 | 0.8
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E, K] | [10, 11, 12] | ctrl | 2030 | 0.5
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E, K] | [10, 11, 12] | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E, K] | [10, 11, 12] | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E, K] | [10, 11, 12] | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, F, K] | 10 | ctrl | 2015 | 0.9
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, F, K] | 10 | ctrl | 2020 | 0.9
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, F, K] | 10 | lower | 2020 | 0.4
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, F, K] | 10 | upper | 2020 | 1.4
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, F, K] | 10 | ctrl | 2030 | 0.9
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, F, K] | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, F, K] | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | [A, F, K] | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2015 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | lower | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | upper | 2020 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2030 | 0
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_i/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_i/y | 2015 | [A, F, K] | 10 | ctrl | 2015 | 1350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_i/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_i/y | 2015 | [A, F, K] | 10 | ctrl | 2020 | 1350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_i/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_i/y | 2015 | [A, F, K] | 10 | lower | 2020 | 550
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_i/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_i/y | 2015 | [A, F, K] | 10 | upper | 2020 | 2150
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_i/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_i/y | 2015 | [A, F, K] | 10 | ctrl | 2030 | 1350
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_i/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_i/y | 2015 | [A, F, K] | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_i/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_i/y | 2015 | [A, F, K] | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_i/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_i/y | 2015 | [A, F, K] | 10 | upper | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [2015-EUR/MWh_i] | Variable O&M | *total, additional to existing plantl | EUR/MWh_i | 2015 | [A, F, K] | 10 | ctrl | 2015 | 0.36
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [2015-EUR/MWh_i] | Variable O&M | *total, additional to existing plantl | EUR/MWh_i | 2015 | [A, F, K] | 10 | ctrl | 2020 | 0.36
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [2015-EUR/MWh_i] | Variable O&M | *total, additional to existing plantl | EUR/MWh_i | 2015 | [A, F, K] | 10 | lower | 2020 | 0.16
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [2015-EUR/MWh_i] | Variable O&M | *total, additional to existing plantl | EUR/MWh_i | 2015 | [A, F, K] | 10 | upper | 2020 | 0.56
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [2015-EUR/MWh_i] | Variable O&M | *total, additional to existing plantl | EUR/MWh_i | 2015 | [A, F, K] | 10 | ctrl | 2030 | 0.36
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [2015-EUR/MWh_i] | Variable O&M | *total, additional to existing plantl | EUR/MWh_i | 2015 | [A, F, K] | 10 | ctrl | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [2015-EUR/MWh_i] | Variable O&M | *total, additional to existing plantl | EUR/MWh_i | 2015 | [A, F, K] | 10 | lower | 2050
03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Technology-specific data | Variable O&M (*total, additional to existing plantl) [2015-EUR/MWh_i] | Variable O&M | *total, additional to existing plantl | EUR/MWh_i | 2015 | [A, F, K] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, J] | 10 | ctrl | 2015 | -0.07
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, J] | 10 | ctrl | 2020 | -0.07
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, J] | 10 | lower | 2020 | -0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, J] | 10 | upper | 2020 | -0.1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, J] | 10 | ctrl | 2030 | -0.07
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, J] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, J] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, J] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2015 | 2.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2020 | 2.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | lower | 2020 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | upper | 2020 | 3
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2030 | 2.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | ctrl | 2015 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | lower | 2020 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | upper | 2020 | 0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, J] | 10 | ctrl | 2015 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, J] | 10 | ctrl | 2020 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, J] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, J] | 10 | upper | 2020 | -0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, J] | 10 | ctrl | 2030 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, J] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, J] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, J] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, J] | 10 | ctrl | 2015 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, J] | 10 | ctrl | 2020 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, J] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, J] | 10 | upper | 2020 | -0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, J] | 10 | ctrl | 2030 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, J] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, J] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, J] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2015 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | lower | 2020 | -0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | upper | 2020 | 0.01
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015 | 300
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020 | 300
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020 | 200
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020 | 400
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030 | 300
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2015 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | upper | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | ctrl | 2015 | 0.03
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | ctrl | 2020 | 0.03
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | lower | 2020 | 0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | upper | 2020 | 0.05
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | ctrl | 2030 | 0.03
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2015 | 15
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2020 | 15
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | lower | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | upper | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2030 | 15
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2015 | 3
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2020 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | upper | 2020 | 0.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2030 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2015 | 10
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2020 | 8
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | lower | 2020 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | upper | 2020 | 20
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2030 | 6
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2015 | 30
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2020 | 24
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | lower | 2020 | 19
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | upper | 2020 | 53
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2030 | 20
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2015 | 0.3
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020 | 0.3
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030 | 0.3
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2015 | 0.98
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020 | 0.98
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030 | 0.98
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2015
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | lower | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | upper | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2030
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2015
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | lower | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | upper | 2020
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2030
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [F, K] | 10 | ctrl | 2015 | 73750
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [F, K] | 10 | ctrl | 2020 | 73750
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [F, K] | 10 | lower | 2020 | 61250
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [F, K] | 10 | upper | 2020 | 86250
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [F, K] | 10 | ctrl | 2030 | 73750
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [F, K] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [F, K] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [F, K] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | [10, 12] | ctrl | 2015 | 1.6107
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | [10, 12] | ctrl | 2020 | 1.6107
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | [10, 12] | lower | 2020 | 1.3423
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | [10, 12] | upper | 2020 | 2.1477
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | [10, 12] | ctrl | 2030 | 1.6107
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | [10, 12] | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | [10, 12] | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | [10, 12] | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [F, K] | 10 | ctrl | 2015 | 2.75
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [F, K] | 10 | ctrl | 2020 | 2.75
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [F, K] | 10 | lower | 2020 | 1.75
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [F, K] | 10 | upper | 2020 | 3.75
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [F, K] | 10 | ctrl | 2030 | 2.75
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [F, K] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [F, K] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [F, K] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, I] | 10 | ctrl | 2015 | 1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, I] | 10 | ctrl | 2020 | 1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, I] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, I] | 10 | upper | 2020 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, I] | 10 | ctrl | 2030 | 1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, I] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, I] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | [A, I] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2015 | 0.0005
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2020 | 0.0005
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | upper | 2020 | 0.001
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, I] | 10 | ctrl | 2015 | -0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, I] | 10 | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, I] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, I] | 10 | upper | 2020 | -0.05
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, I] | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, I] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, I] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | [A, I] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, I] | 10 | ctrl | 2015 | -0.02
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, I] | 10 | ctrl | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, I] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, I] | 10 | upper | 2020 | -0.05
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, I] | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, I] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, I] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | [A, I] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, I] | 10 | ctrl | 2015 | 0.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, I] | 10 | ctrl | 2020 | 0.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, I] | 10 | lower | 2020 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, I] | 10 | upper | 2020 | 2
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, I] | 10 | ctrl | 2030 | 0
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, I] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, I] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | [A, I] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | [F, K] | 10 | ctrl | 2015 | 29500
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | [F, K] | 10 | ctrl | 2020 | 29500
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | [F, K] | 10 | lower | 2020 | 24500
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | [F, K] | 10 | upper | 2020 | 34500
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | [F, K] | 10 | ctrl | 2030 | 29500
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | [F, K] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | [F, K] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | [F, K] | 10 | upper | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | [F, K] | 10 | ctrl | 2015 | 1.1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | [F, K] | 10 | ctrl | 2020 | 1.1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | [F, K] | 10 | lower | 2020 | 0.7
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | [F, K] | 10 | upper | 2020 | 1.5
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | [F, K] | 10 | ctrl | 2030 | 1.1
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | [F, K] | 10 | ctrl | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | [F, K] | 10 | lower | 2050
03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | [F, K] | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, I] | 10 | ctrl | 2015 | -0.07
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, I] | 10 | ctrl | 2020 | -0.07
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, I] | 10 | lower | 2020 | -0.02
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, I] | 10 | upper | 2020 | -0.1
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, I] | 10 | ctrl | 2030 | -0.07
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, I] | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, I] | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C, additional to existing plant) | Cb coefficient | 50°C/100°C, additional to existing plant |  |  | [A, B, I] | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2015 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2020 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | lower | 2020 | 1.5
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | upper | 2020 | 2.5
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2030 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | lower | 2020 | -0.01
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | upper | 2020 | 0.01
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C, additional to existing plant) | Cv coefficient | 50°C/100°C, additional to existing plant |  |  | A | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, I] | 10 | ctrl | 2015 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, I] | 10 | ctrl | 2020 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, I] | 10 | lower | 2020 | -0.02
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, I] | 10 | upper | 2020 | -0.04
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, I] | 10 | ctrl | 2030 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, I] | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, I] | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average, additional to existing plant) [] | Electrical efficiency | net, annual average, additional to existing plant | [] |  | [A, B, I] | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, I] | 10 | ctrl | 2015 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, I] | 10 | ctrl | 2020 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, I] | 10 | lower | 2020 | -0.02
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, I] | 10 | upper | 2020 | -0.04
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, I] | 10 | ctrl | 2030 | -0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, I] | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, I] | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate, additional to existing plant) [] | Electrical efficiency | net, name plate, additional to existing plant | [] |  | [A, B, I] | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | lower | 2020 | -0.01
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | upper | 2020 | 0.01
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Forced outage (additional to existing plant) [] | Forced outage | additional to existing plant | [] |  | A | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015 | 300
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020 | 300
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020 | 200
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020 | 400
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030 | 300
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Planned outage (additional to existing plant) [weeks per year] | Planned outage | additional to existing plant | weeks per year |  | A | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | ctrl | 2015 | 0.04
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | ctrl | 2020 | 0.04
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | lower | 2020 | 0.03
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | upper | 2020 | 0.06
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | ctrl | 2030 | 0.04
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Space requirement (additional to existing plant) [1000 m2/MW_e] | Space requirement | additional to existing plant | 1000 m2/MW_e |  | [A, D] | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2015 | 15
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2020 | 15
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | lower | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | upper | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2030 | 15
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | C | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2015 | 3
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2020 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | lower | 2020 | 3.1
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | upper | 2020 | 3.1
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2030 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G |  | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2015 | 10
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2020 | 8
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | lower | 2020 | 0.8
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | upper | 2020 | 0.8
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2030 | 6
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G |  | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2015 | 30
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2020 | 24
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | lower | 2020 | 19
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | upper | 2020 | 53
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2030 | 20
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G |  | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G |  | ctrl | 2015 | 0.3
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G |  | ctrl | 2020 | 0.3
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G |  | lower | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G |  | upper | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G |  | ctrl | 2030 | 0.3
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G |  | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G |  | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G |  | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G |  | ctrl | 2015 | 0.98
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G |  | ctrl | 2020 | 0.98
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G |  | lower | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G |  | upper | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G |  | ctrl | 2030 | 0.98
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G |  | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G |  | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G |  | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2015
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | lower | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | upper | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2030
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2015
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | lower | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | upper | 2020
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2030
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | F | 10 | ctrl | 2015 | 14175
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | F | 10 | ctrl | 2020 | 14175
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | F | 10 | lower | 2020 | 12600
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | F | 10 | upper | 2020 | 15750
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | F | 10 | ctrl | 2030 | 14175
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | F | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | F | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Fixed O&M (*total, additional to existing plant) [2015-EUR/MW_e/y] | Fixed O&M | *total, additional to existing plant | EUR/MW_e/y | 2015 | F | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 10 | ctrl | 2015 | 1.6107
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 10 | ctrl | 2020 | 1.6107
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 10 | lower | 2020 | 1.3423
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 10 | upper | 2020 | 2.1477
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 10 | ctrl | 2030 | 1.6107
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | F | 10 | ctrl | 2015 | 1.5
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | F | 10 | ctrl | 2020 | 1.5
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | F | 10 | lower | 2020 | 1
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | F | 10 | upper | 2020 | 2
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | F | 10 | ctrl | 2030 | 1.5
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | F | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | F | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Variable O&M (*total, additional to existing plant) [2015-EUR/MWh_e] | Variable O&M | *total, additional to existing plant | EUR/MWh_e | 2015 | F | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Cold start-up time (additional to existing plant) [hours] | Cold start-up time | additional to existing plant | hours |  | A | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Minimum load (of full load, additional to existing plant) [] | Minimum load | of full load, additional to existing plant | [] |  | A | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Primary regulation (of full load, additional to existing plant, per 30 seconds) [] | Primary regulation | of full load, additional to existing plant, per 30 seconds | [] |  | A | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Secondary regulation (of full load, additional to existing plant, per minute) [] | Secondary regulation | of full load, additional to existing plant, per minute | [] |  | A | 10 | upper | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2015 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | lower | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | upper | 2020 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2030 | 0
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | ctrl | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | lower | 2050
03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Regulation ability | Warm start-up time (additional to existing plant) [hours] | Warm start-up time | additional to existing plant | hours |  | A | 10 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | B | 13 | ctrl | 2015 | 0.35
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | B | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | B | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | B | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | B | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | B | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | B | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | B | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 13 | ctrl | 2015
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | 13 | ctrl | 2015 | 0.0027
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 13 | ctrl | 2015
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C | 13 | ctrl | 2015 | 0.03
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, E] | 13 | ctrl | 2015 | 70
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, E] | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, E] | 13 | lower | 2020 | 50
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, E] | 13 | upper | 2020 | 90
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, E] | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, E] | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, E] | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, E] | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 13 | ctrl | 2015 | 1.5643
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2015 | 15
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | C | 13 | ctrl | 2015 | 3
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | C | 13 | ctrl | 2015 | 10
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | C | 13 | ctrl | 2015 | 30
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | C | 13 | ctrl | 2015 | 0.3
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2015
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2015
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  |  | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2015
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  |  | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | D |  | ctrl | 2015 | 109259.2593
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | D |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | D |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | D |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | D |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | D |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | D |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | D |  | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | ctrl | 2015
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | D |  | ctrl | 2015 | 4.0741
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | D |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | D |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | D |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | D |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | D |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | D |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | D |  | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | C | 13 | ctrl | 2015 | 12
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | C | 13 | ctrl | 2015 | 0.45
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C | 13 | ctrl | 2015 | 0.02
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 13 | ctrl | 2015 | 0.03
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | 13 | ctrl | 2015 | 2
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | 13 | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | 13 | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | 13 | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | 13 | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | 13 | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | 13 | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | 13 | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | D |  | ctrl | 2015 | 29500
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | D |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | D |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | D |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | D |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | D |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | D |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | D |  | upper | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | D |  | ctrl | 2015 | 1.1
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | D |  | ctrl | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | D |  | lower | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | D |  | upper | 2020
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | D |  | ctrl | 2030
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | D |  | ctrl | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | D |  | lower | 2050
03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | D |  | upper | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | ctrl | 2015 | 0.95
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | ctrl | 2020 | 0.96
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | lower | 2020 | 0.8
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | upper | 2020 | 1.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | ctrl | 2030 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | ctrl | 2050 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | lower | 2050 | 0.8
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | upper | 2050 | 1.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2015 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2020 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | lower | 2020 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | upper | 2020 | 2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2030 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2050 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | lower | 2050 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | upper | 2050 | 2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2015
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | lower | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | upper | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2030
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | lower | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | upper | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [6, 12] | ctrl | 2015 | 0.41
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [6, 12] | ctrl | 2020 | 0.42
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [6, 12] | lower | 2020 | 0.38
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [6, 12] | upper | 2020 | 0.42
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [6, 12] | ctrl | 2030 | 0.43
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [6, 12] | ctrl | 2050 | 0.45
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [6, 12] | lower | 2050 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | [6, 12] | upper | 2050 | 0.44
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | ctrl | 2015 | 0.39
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | ctrl | 2020 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | lower | 2020 | 0.36
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | upper | 2020 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | ctrl | 2030 | 0.41
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | ctrl | 2050 | 0.43
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | lower | 2050 | 0.38
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | upper | 2050 | 0.42
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | ctrl | 2015 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | ctrl | 2020 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | lower | 2020 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | upper | 2020 | 0.03
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | ctrl | 2030 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | ctrl | 2050 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | lower | 2050 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | upper | 2050 | 0.03
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2015
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | lower | 2020 | 40
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | upper | 2020 | 125
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2030
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | lower | 2050 | 40
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | upper | 2050 | 125
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | ctrl | 2015 | 3
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | ctrl | 2020 | 3
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | lower | 2020 | 2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | upper | 2020 | 3.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | ctrl | 2030 | 2.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | ctrl | 2050 | 2.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | lower | 2050 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | upper | 2050 | 3
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | ctrl | 2015 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | ctrl | 2020 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | lower | 2020 | 0.015
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | upper | 2020 | 0.03
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | ctrl | 2030 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | ctrl | 2050 | 0.02
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | lower | 2050 | 0.015
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | upper | 2050 | 0.03
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | ctrl | 2015 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | ctrl | 2020 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | lower | 2020 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | upper | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | ctrl | 2030 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | ctrl | 2050 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | lower | 2050 | 25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | upper | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 9 | ctrl | 2015 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 9 | ctrl | 2020 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 9 | lower | 2020 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 9 | upper | 2020 | 8
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 9 | ctrl | 2030 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 9 | ctrl | 2050 | 1.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 9 | lower | 2050 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 9 | upper | 2050 | 8
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 9 | ctrl | 2015 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 9 | ctrl | 2020 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 9 | lower | 2020 | 0.7
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 9 | upper | 2020 | 1.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 9 | ctrl | 2030 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 9 | ctrl | 2050 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 9 | lower | 2050 | 0.7
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 9 | upper | 2050 | 1.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | ctrl | 2015 | 20
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | ctrl | 2020 | 15
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | lower | 2020 | 10
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | upper | 2020 | 30
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | ctrl | 2030 | 10
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | ctrl | 2050 | 10
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | lower | 2050 | 7.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | upper | 2050 | 20
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2015 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | ctrl | 2015 | 20000
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | ctrl | 2020 | 19500
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | lower | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | upper | 2020
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | ctrl | 2030 | 18600
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | ctrl | 2050 | 18000
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | lower | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | upper | 2050
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | ctrl | 2015 | 0.6
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | ctrl | 2020 | 0.59
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | lower | 2020 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | upper | 2020 | 0.9
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | ctrl | 2030 | 0.56
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | ctrl | 2050 | 0.52
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | lower | 2050 | 0.35
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | upper | 2050 | 0.85
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | ctrl | 2015 | 4.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | ctrl | 2020 | 4.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | lower | 2020 | 4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | upper | 2020 | 6
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | ctrl | 2030 | 4.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | ctrl | 2050 | 4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | lower | 2050 | 3
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | upper | 2050 | 5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | lower | 2020 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | upper | 2020 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | lower | 2050 | 0.4
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | upper | 2050 | 1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | ctrl | 2015 | 0.25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | ctrl | 2020 | 0.23
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | lower | 2020 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | upper | 2020 | 0.25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | ctrl | 2030 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | ctrl | 2050 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | lower | 2050 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | upper | 2050 | 0.25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2015 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | lower | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | upper | 2020 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2030 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | lower | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | upper | 2050 | 0
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | ctrl | 2015 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | ctrl | 2020 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | lower | 2020 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | upper | 2020 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | ctrl | 2030 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | ctrl | 2050 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | lower | 2050 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | upper | 2050 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.25
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.23
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | lower | 2020 | 0.1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | upper | 2020 | 0.5
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.2
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | lower | 2050 | 0.1
04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | upper | 2050 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | ctrl | 2015 | 0.71
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | ctrl | 2020 | 0.73
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | lower | 2020 | 0.61
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | upper | 2020 | 0.8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | ctrl | 2030 | 0.8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | ctrl | 2050 | 0.8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | lower | 2050 | 0.7
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [6, 12] | upper | 2050 | 0.9
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2015 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2020 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | lower | 2020 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | upper | 2020 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2030 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | ctrl | 2050 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | lower | 2050 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 6 | upper | 2050 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2015
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | lower | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | upper | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2030
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | lower | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | upper | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [G, H] | [6, 12] | ctrl | 2015 | 0.36
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [G, H] | [6, 12] | ctrl | 2020 | 0.37
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [G, H] | [6, 12] | lower | 2020 | 0.32
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [G, H] | [6, 12] | upper | 2020 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [G, H] | [6, 12] | ctrl | 2030 | 0.39
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [G, H] | [6, 12] | ctrl | 2050 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [G, H] | [6, 12] | lower | 2050 | 0.34
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [G, H] | [6, 12] | upper | 2050 | 0.42
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | ctrl | 2015 | 0.34
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | ctrl | 2020 | 0.35
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | lower | 2020 | 0.3
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | upper | 2020 | 0.38
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | ctrl | 2030 | 0.37
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | ctrl | 2050 | 0.38
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | lower | 2050 | 0.32
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [6, 11] | upper | 2050 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | ctrl | 2015 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | ctrl | 2020 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | lower | 2020 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | upper | 2020 | 0.03
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | ctrl | 2030 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | ctrl | 2050 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | lower | 2050 | 0.02
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 6 | upper | 2050 | 0.03
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2015
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | lower | 2020 | 5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | upper | 2020 | 40
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2030
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | lower | 2050 | 5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | upper | 2050 | 40
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | ctrl | 2015 | 3
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | ctrl | 2020 | 2.8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | lower | 2020 | 2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | upper | 2020 | 3.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | ctrl | 2030 | 2.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | ctrl | 2050 | 2.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | lower | 2050 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 6 | upper | 2050 | 3
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | ctrl | 2015 | 0.04
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | ctrl | 2020 | 0.04
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | lower | 2020 | 0.03
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | upper | 2020 | 0.07
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | ctrl | 2030 | 0.04
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | ctrl | 2050 | 0.04
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | lower | 2050 | 0.03
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 7 | upper | 2050 | 0.07
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | ctrl | 2015 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | ctrl | 2020 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | lower | 2020 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | upper | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | ctrl | 2030 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | ctrl | 2050 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | lower | 2050 | 25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [6, 7] | upper | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 9 | ctrl | 2015 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 9 | ctrl | 2020 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 9 | lower | 2020 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 9 | upper | 2020 | 8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 9 | ctrl | 2030 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 9 | ctrl | 2050 | 1.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 9 | lower | 2050 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 9 | upper | 2050 | 8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 9 | ctrl | 2015 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 9 | ctrl | 2020 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 9 | lower | 2020 | 0.7
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 9 | upper | 2020 | 1.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 9 | ctrl | 2030 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 9 | ctrl | 2050 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 9 | lower | 2050 | 0.7
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 9 | upper | 2050 | 1.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | ctrl | 2015 | 20
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | ctrl | 2020 | 15
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | lower | 2020 | 10
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | upper | 2020 | 30
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | ctrl | 2030 | 10
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | ctrl | 2050 | 10
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | lower | 2050 | 8
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [7, 9] | upper | 2050 | 20
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | ctrl | 2015 | 20000
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | ctrl | 2020 | 19500
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | lower | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | upper | 2020
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | ctrl | 2030 | 18600
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | ctrl | 2050 | 18000
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | lower | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 6 | upper | 2050
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | ctrl | 2015 | 0.75
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | ctrl | 2020 | 0.73
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | lower | 2020 | 0.6
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | upper | 2020 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | ctrl | 2030 | 0.7
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | ctrl | 2050 | 0.68
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | lower | 2050 | 0.55
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | upper | 2050 | 0.95
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | ctrl | 2015 | 5.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | ctrl | 2020 | 5.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | lower | 2020 | 5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | upper | 2020 | 7
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | ctrl | 2030 | 5.1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | ctrl | 2050 | 4.6
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | lower | 2050 | 4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 6 | upper | 2050 | 6
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | lower | 2020 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | upper | 2020 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | lower | 2050 | 0.4
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 8] | upper | 2050 | 1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | ctrl | 2015 | 0.25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | ctrl | 2020 | 0.23
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | lower | 2020 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | upper | 2020 | 0.25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | ctrl | 2030 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | ctrl | 2050 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | lower | 2050 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | 6 | upper | 2050 | 0.25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | lower | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | upper | 2020 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | lower | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | upper | 2050 | 0
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | ctrl | 2015 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | ctrl | 2020 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | lower | 2020 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | upper | 2020 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | ctrl | 2030 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | ctrl | 2050 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | lower | 2050 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | 6 | upper | 2050 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2015 | 0.25
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2020 | 0.23
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | lower | 2020 | 0.1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | upper | 2020 | 0.5
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2030 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | ctrl | 2050 | 0.2
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | lower | 2050 | 0.1
04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  | [5, 6, 8] | upper | 2050 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [7, 13] | ctrl | 2015 | 0.6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [7, 13] | ctrl | 2020 | 0.6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [7, 13] | lower | 2020 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [7, 13] | upper | 2020 | 0.85
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [7, 13] | ctrl | 2030 | 0.6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [7, 13] | ctrl | 2050 | 0.6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [7, 13] | lower | 2050 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [7, 13] | upper | 2050 | 0.85
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Construction time [years] | Construction time |  | years |  | L | 13 | ctrl | 2015 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Construction time [years] | Construction time |  | years |  | L | 13 | ctrl | 2020 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Construction time [years] | Construction time |  | years |  | L | 13 | lower | 2020 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Construction time [years] | Construction time |  | years |  | L | 13 | upper | 2020 | 0.8
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Construction time [years] | Construction time |  | years |  | L | 13 | ctrl | 2030 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Construction time [years] | Construction time |  | years |  | L | 13 | ctrl | 2050 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Construction time [years] | Construction time |  | years |  | L | 13 | lower | 2050 | 0.2
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Construction time [years] | Construction time |  | years |  | L | 13 | upper | 2050 | 0.7
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2015
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2030
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | upper | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | M | 7 | ctrl | 2015 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | M | 7 | ctrl | 2020 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | M | 7 | lower | 2020 | 0.23
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | M | 7 | upper | 2020 | 0.32
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | M | 7 | ctrl | 2030 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | M | 7 | ctrl | 2050 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | M | 7 | lower | 2050 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | M | 7 | upper | 2050 | 0.35
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  |  | ctrl | 2015 | 0.28
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  |  | ctrl | 2020 | 0.28
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  |  | lower | 2020 | 0.21
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  |  | upper | 2020 | 0.29
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  |  | ctrl | 2030 | 0.28
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  |  | ctrl | 2050 | 0.28
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  |  | lower | 2050 | 0.23
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  |  | upper | 2050 | 0.33
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020 | 0.015
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020 | 0.2
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050 | 0.015
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050 | 0.2
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 7 | ctrl | 2015 | 0.06
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 7 | ctrl | 2020 | 0.06
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 7 | lower | 2020 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 7 | upper | 2020 | 0.15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 7 | ctrl | 2030 | 0.06
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 7 | ctrl | 2050 | 0.06
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 7 | lower | 2050 | 0.05
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 7 | upper | 2050 | 0.15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | L |  | ctrl | 2015 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | L |  | ctrl | 2020 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | L |  | lower | 2020 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | L |  | upper | 2020 | 20
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | L |  | ctrl | 2030 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | L |  | ctrl | 2050 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | L |  | lower | 2050 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | L |  | upper | 2050 | 20
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 13 | ctrl | 2015 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 13 | ctrl | 2020 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 13 | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 13 | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 13 | ctrl | 2030 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 13 | ctrl | 2050 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 13 | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 13 | upper | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 13 | ctrl | 2015
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 13 | ctrl | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 13 | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 13 | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 13 | ctrl | 2030
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 13 | ctrl | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 13 | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 13 | upper | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [7, 13] | ctrl | 2015 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [7, 13] | ctrl | 2020 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [7, 13] | lower | 2020 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [7, 13] | upper | 2020 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [7, 13] | ctrl | 2030 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [7, 13] | ctrl | 2050 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [7, 13] | lower | 2050 | 6
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [7, 13] | upper | 2050 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 13 | ctrl | 2015 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 13 | ctrl | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 13 | lower | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 13 | upper | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 13 | ctrl | 2030 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 13 | ctrl | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 13 | lower | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 13 | upper | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2015 | 0.85
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2020 | 0.85
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [13, 14] | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [13, 14] | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2030 | 0.8
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2050 | 0.7
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [13, 14] | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [13, 14] | upper | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2015 | 0.35
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2020 | 0.35
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [13, 14] | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [13, 14] | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2030 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2050 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [13, 14] | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [13, 14] | upper | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2015 | 1.2
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2020 | 1.2
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [13, 14] | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [13, 14] | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2030 | 1.1
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2050 | 1
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [13, 14] | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [13, 14] | upper | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 13 | ctrl | 2015 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 13 | ctrl | 2020 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 13 | lower | 2020 | 10
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 13 | upper | 2020 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 13 | ctrl | 2030 | 14
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 13 | ctrl | 2050 | 13
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 13 | lower | 2050 | 8
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 13 | upper | 2050 | 15
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2015 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2020 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2030 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2050 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | L | [7, 13] | ctrl | 2015 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | L | [7, 13] | ctrl | 2020 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | L | [7, 13] | lower | 2020 | 0.3
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | L | [7, 13] | upper | 2020 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | L | [7, 13] | ctrl | 2030 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | L | [7, 13] | ctrl | 2050 | 0.4
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | L | [7, 13] | lower | 2050 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | L | [7, 13] | upper | 2050 | 0.5
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2015 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2020 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050 | 0
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2015 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2020
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050 | 0.25
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015 | 1.7
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020 | 1.8
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020 | 2.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050 | 2.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050 | 2.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2015 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2020 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2020 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2020 | 3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2030 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2050 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2050 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2050 | 3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2015 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2020 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | lower | 2020
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | upper | 2020
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2030 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | ctrl | 2050 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | lower | 2050
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | J |  | upper | 2050
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2015 | 0.58
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2020 | 0.59
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | lower | 2020 | 0.55
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | upper | 2020 | 0.61
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2030 | 0.61
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2050 | 0.63
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | lower | 2050 | 0.58
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | upper | 2050 | 0.65
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | ctrl | 2015 | 0.55
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | ctrl | 2020 | 0.56
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | lower | 2020 | 0.52
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | upper | 2020 | 0.58
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | ctrl | 2030 | 0.58
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | ctrl | 2050 | 0.6
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | lower | 2050 | 0.55
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | upper | 2050 | 0.62
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2015 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2020 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2020 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2020 | 0.04
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2030 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2050 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2050 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2050 | 0.04
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2015
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2020
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | lower | 2020 | 100
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | upper | 2020 | 500
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2030
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2050
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | lower | 2050 | 100
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | upper | 2050 | 500
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2015 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2020 | 2.3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2020 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2020 | 4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2030 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2050 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2050 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2050 | 4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | ctrl | 2015 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | ctrl | 2020 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | lower | 2020 | 0.015
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | upper | 2020 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | ctrl | 2030 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | ctrl | 2050 | 0.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | lower | 2050 | 0.015
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | upper | 2050 | 0.03
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | ctrl | 2015 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | ctrl | 2020 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | lower | 2020 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | upper | 2020
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | ctrl | 2030 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | ctrl | 2050 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | lower | 2050 | 25
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | upper | 2050
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | ctrl | 2015 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | ctrl | 2020 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | lower | 2020 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | upper | 2020 | 8
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | ctrl | 2030 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | ctrl | 2050 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | lower | 2050 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | upper | 2050 | 8
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | ctrl | 2015 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | ctrl | 2020 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | lower | 2020 | 0.7
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | upper | 2020 | 1.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | ctrl | 2030 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | ctrl | 2050 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | lower | 2050 | 0.7
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | upper | 2050 | 1.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | ctrl | 2015 | 20
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | ctrl | 2020 | 15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | lower | 2020 | 10
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | upper | 2020 | 30
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | ctrl | 2030 | 10
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | ctrl | 2050 | 8
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | lower | 2050 | 5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | upper | 2050 | 15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2015 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2020 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2020 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050 | 0
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | ctrl | 2015 | 0.7
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | ctrl | 2020 | 0.68
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | lower | 2020 | 0.65
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | upper | 2020 | 1.02
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | ctrl | 2030 | 0.64
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | ctrl | 2050 | 0.61
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | lower | 2050 | 0.6
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | upper | 2050 | 0.95
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | ctrl | 2015 | 0.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | ctrl | 2020 | 0.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | lower | 2020 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | upper | 2020 | 0.18
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | ctrl | 2030 | 0.19
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | ctrl | 2050 | 0.19
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | lower | 2050 | 0.1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | upper | 2050 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | ctrl | 2015 | 30000
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | ctrl | 2020 | 29300
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | lower | 2020 | 25000
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | upper | 2020 | 35000
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | ctrl | 2030 | 27800
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | ctrl | 2050 | 26000
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | lower | 2050 | 20000
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | upper | 2050 | 30000
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 8] | ctrl | 2015 | 0.9
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 8] | ctrl | 2020 | 0.88
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 8] | lower | 2020 | 0.8
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 8] | upper | 2020 | 1.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 8] | ctrl | 2030 | 0.83
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 8] | ctrl | 2050 | 0.8
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 8] | lower | 2050 | 0.7
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 8] | upper | 2050 | 1.1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | ctrl | 2015 | 4.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | ctrl | 2020 | 4.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | lower | 2020 | 3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | upper | 2020 | 7
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | ctrl | 2030 | 4.2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | ctrl | 2050 | 4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | lower | 2050 | 3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | upper | 2050 | 7
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | ctrl | 2015 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | ctrl | 2020 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | lower | 2020 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | upper | 2020 | 5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | ctrl | 2030 | 2.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | ctrl | 2050 | 2
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | lower | 2050 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | upper | 2050 | 5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | ctrl | 2015 | 0.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | ctrl | 2020 | 0.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | lower | 2020 | 0.3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | upper | 2020 | 0.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | ctrl | 2030 | 0.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | ctrl | 2050 | 0.4
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | lower | 2050 | 0.3
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | upper | 2050 | 0.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | K |  | ctrl | 2015
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | K |  | ctrl | 2020
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | K |  | lower | 2020
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | K |  | upper | 2020
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | K |  | ctrl | 2030
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | K |  | ctrl | 2050
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | K |  | lower | 2050
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | K |  | upper | 2050
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  | [5, 3, 11] | ctrl | 2015 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  | [5, 3, 11] | ctrl | 2020 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  | [5, 3, 11] | lower | 2020 | 0.05
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  | [5, 3, 11] | upper | 2020 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  | [5, 3, 11] | ctrl | 2030 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  | [5, 3, 11] | ctrl | 2050 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  | [5, 3, 11] | lower | 2050 | 0.05
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  | [5, 3, 11] | upper | 2050 | 0.15
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | ctrl | 2015 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | ctrl | 2020 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | lower | 2020 | 0.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | upper | 2020 | 1.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | ctrl | 2030 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | ctrl | 2050 | 1
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | lower | 2050 | 0.5
05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | upper | 2050 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015 | 1.2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020 | 1.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020 | 0.9
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020 | 1.6
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030 | 1.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050 | 1.55
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050 | 1.1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050 | 1.7
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2015 | 2.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2020 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2020 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2020 | 3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2030 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2050 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2050 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2050 | 3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | L |  | ctrl | 2015
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | L |  | ctrl | 2020
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | L |  | lower | 2020
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | L |  | upper | 2020
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | L |  | ctrl | 2030
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | L |  | ctrl | 2050
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | L |  | lower | 2050
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | L |  | upper | 2050
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2015 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2020 | 0.51
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | lower | 2020 | 0.42
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | upper | 2020 | 0.55
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2030 | 0.53
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2050 | 0.55
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | lower | 2050 | 0.45
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | upper | 2050 | 0.58
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | ctrl | 2015 | 0.47
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | ctrl | 2020 | 0.48
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | lower | 2020 | 0.39
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | upper | 2020 | 0.52
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | ctrl | 2030 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | ctrl | 2050 | 0.52
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | lower | 2050 | 0.42
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  |  | [5, 9] | upper | 2050 | 0.55
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2015 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2020 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2020 | 0.02
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2020 | 0.04
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2030 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2050 | 0.03
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2050 | 0.02
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2050 | 0.04
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2015
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2020
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | lower | 2020 | 10
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | upper | 2020 | 100
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2030
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | ctrl | 2050
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | lower | 2050 | 10
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | F |  | upper | 2050 | 100
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2015 | 2.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2020 | 2.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2020 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2020 | 4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2030 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2050 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2050 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2050 | 4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | ctrl | 2015 | 0.025
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | ctrl | 2020 | 0.025
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | lower | 2020 | 0.019
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | upper | 2020 | 0.038
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | ctrl | 2030 | 0.025
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | ctrl | 2050 | 0.025
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | lower | 2050 | 0.019
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | G | 3 | upper | 2050 | 0.038
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | ctrl | 2015 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | ctrl | 2020 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | lower | 2020 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | upper | 2020
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | ctrl | 2030 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | ctrl | 2050 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | lower | 2050 | 25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | E | [5, 3] | upper | 2050
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | ctrl | 2015 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | ctrl | 2020 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | lower | 2020 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | upper | 2020 | 8
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | ctrl | 2030 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | ctrl | 2050 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | lower | 2050 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 7 | upper | 2050 | 8
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | ctrl | 2015 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | ctrl | 2020 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | lower | 2020 | 0.7
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | upper | 2020 | 1.2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | ctrl | 2030 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | ctrl | 2050 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | lower | 2050 | 0.7
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 7 | upper | 2050 | 1.2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | ctrl | 2015 | 20
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | ctrl | 2020 | 15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | lower | 2020 | 10
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | upper | 2020 | 30
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | ctrl | 2030 | 10
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | ctrl | 2050 | 8
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | lower | 2050 | 5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | D | [3, 7] | upper | 2050 | 15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2015 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2020 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2020 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050 | 0
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | ctrl | 2015 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | ctrl | 2020 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | lower | 2020 | 0.8
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | upper | 2020 | 1.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | ctrl | 2030 | 0.9
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | ctrl | 2050 | 0.8
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | lower | 2050 | 0.65
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 10 | upper | 2050 | 1.25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | ctrl | 2015 | 0.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | ctrl | 2020 | 0.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | lower | 2020 | 0.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | upper | 2020 | 0.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | ctrl | 2030 | 0.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | ctrl | 2050 | 0.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | lower | 2050 | 0.25
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 10 | upper | 2050 | 0.35
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | ctrl | 2015 | 30000
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | ctrl | 2020 | 29300
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | lower | 2020 | 25000
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | upper | 2020 | 35000
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | ctrl | 2030 | 27800
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | ctrl | 2050 | 26000
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | lower | 2050 | 20000
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | B | 5 | upper | 2050 | 30000
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 9] | ctrl | 2015 | 1.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 9] | ctrl | 2020 | 1.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 9] | lower | 2020 | 1.1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 9] | upper | 2020 | 1.8
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 9] | ctrl | 2030 | 1.2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 9] | ctrl | 2050 | 1.1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 9] | lower | 2050 | 0.9
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 9] | upper | 2050 | 1.6
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | ctrl | 2015 | 4.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | ctrl | 2020 | 4.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | lower | 2020 | 3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | upper | 2020 | 7
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | ctrl | 2030 | 4.2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | ctrl | 2050 | 4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | lower | 2050 | 3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  | 5 | upper | 2050 | 7
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | ctrl | 2015 | 2.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | ctrl | 2020 | 2.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | lower | 2020 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | upper | 2020 | 5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | ctrl | 2030 | 2.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | ctrl | 2050 | 2
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | lower | 2050 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | [5, 6, 1, 11] | upper | 2050 | 5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | ctrl | 2015 | 0.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | ctrl | 2020 | 0.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | lower | 2020 | 0.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | upper | 2020 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | ctrl | 2030 | 0.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | ctrl | 2050 | 0.4
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | lower | 2050 | 0.3
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | A | [5, 3, 11] | upper | 2050 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2015
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2020
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | lower | 2020
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | upper | 2020
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2030
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | ctrl | 2050
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | lower | 2050
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | I |  | upper | 2050
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [C, M] | [5, 3, 11] | ctrl | 2015 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [C, M] | [5, 3, 11] | ctrl | 2020 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [C, M] | [5, 3, 11] | lower | 2020 | 0.05
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [C, M] | [5, 3, 11] | upper | 2020 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [C, M] | [5, 3, 11] | ctrl | 2030 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [C, M] | [5, 3, 11] | ctrl | 2050 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [C, M] | [5, 3, 11] | lower | 2050 | 0.05
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [C, M] | [5, 3, 11] | upper | 2050 | 0.15
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | ctrl | 2015 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | ctrl | 2020 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | lower | 2020 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | upper | 2020 | 1.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | ctrl | 2030 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | ctrl | 2050 | 1
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | lower | 2050 | 0.5
05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [5, 6, 1, 11] | upper | 2050 | 1.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | ctrl | 2015 | 0.9
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | ctrl | 2020 | 0.95
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | lower | 2020 | 0.65
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | upper | 2020 | 1.02
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | ctrl | 2030 | 0.99
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | ctrl | 2050 | 1.04
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | lower | 2050 | 0.65
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | upper | 2050 | 1.15
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | ctrl | 2015 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | ctrl | 2020 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | lower | 2020 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | upper | 2020 | 1.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | ctrl | 2030 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | ctrl | 2050 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | lower | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | upper | 2050 | 1.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | ctrl | 2015
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | ctrl | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | lower | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | upper | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | ctrl | 2030
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | ctrl | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | lower | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | upper | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | ctrl | 2015 | 0.46
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | ctrl | 2020 | 0.47
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | lower | 2020 | 0.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | upper | 2020 | 0.48
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | ctrl | 2030 | 0.48
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | ctrl | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | lower | 2050 | 0.44
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | upper | 2050 | 0.52
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | ctrl | 2015 | 0.44
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | ctrl | 2020 | 0.45
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | lower | 2020 | 0.38
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | upper | 2020 | 0.46
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | ctrl | 2030 | 0.47
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | ctrl | 2050 | 0.48
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | lower | 2050 | 0.42
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | upper | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | ctrl | 2015 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | ctrl | 2020 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | lower | 2020 | 0.02
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | upper | 2020 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | ctrl | 2030 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | ctrl | 2050 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | lower | 2050 | 0.02
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | upper | 2050 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020 | 10
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050 | 10
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | ctrl | 2015 | 0.8
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | ctrl | 2020 | 0.8
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | lower | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | upper | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | ctrl | 2030 | 0.8
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | ctrl | 2050 | 0.8
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | lower | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | upper | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.04
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.04
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.035
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.03
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.025
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.04
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | ctrl | 2015 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | ctrl | 2020 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | lower | 2020 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | upper | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | ctrl | 2030 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | ctrl | 2050 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | lower | 2050 | 25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | upper | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | ctrl | 2015 | 315
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | ctrl | 2020 | 315
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | lower | 2020 | 300
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | upper | 2020 | 400
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | ctrl | 2030 | 280
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | ctrl | 2050 | 250
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | lower | 2050 | 250
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | upper | 2050 | 350
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | H |  | ctrl | 2015 | 0.6
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | H |  | ctrl | 2020 | 0.6
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | H |  | lower | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | H |  | upper | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | H |  | ctrl | 2030 | 0.6
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | H |  | ctrl | 2050 | 0.6
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | H |  | lower | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | H |  | upper | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | ctrl | 2015 | 75
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | ctrl | 2020 | 60
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | lower | 2020 | 50
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | upper | 2020 | 100
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | ctrl | 2030 | 60
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | ctrl | 2050 | 60
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | lower | 2050 | 50
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | upper | 2050 | 100
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 4 | ctrl | 2015 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 4 | ctrl | 2020 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 4 | lower | 2020 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 4 | upper | 2020 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 4 | ctrl | 2030 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 4 | ctrl | 2050 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 4 | lower | 2050 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 4 | upper | 2050 | 0
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | H | [3, 5] | ctrl | 2015 | 0.65
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | H | [3, 5] | ctrl | 2020 | 0.6
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | H | [3, 5] | lower | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | H | [3, 5] | upper | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | H | [3, 5] | ctrl | 2030 | 0.55
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | H | [3, 5] | ctrl | 2050 | 0.55
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | H | [3, 5] | lower | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | H | [3, 5] | upper | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | H | [3, 5] | ctrl | 2015 | 0.35
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | H | [3, 5] | ctrl | 2020 | 0.35
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | H | [3, 5] | lower | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | H | [3, 5] | upper | 2020
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | H | [3, 5] | ctrl | 2030 | 0.35
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | H | [3, 5] | ctrl | 2050 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | H | [3, 5] | lower | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | H | [3, 5] | upper | 2050
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | ctrl | 2015 | 10000
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | ctrl | 2020 | 9750
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | lower | 2020 | 7000
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | upper | 2020 | 20000
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | ctrl | 2030 | 9300
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | ctrl | 2050 | 8500
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | lower | 2050 | 6000
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | upper | 2050 | 15000
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | ctrl | 2015 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | ctrl | 2020 | 0.95
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | lower | 2020 | 0.9
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | upper | 2020 | 1.1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | ctrl | 2030 | 0.9
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | ctrl | 2050 | 0.85
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | lower | 2050 | 0.8
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | upper | 2050 | 1.1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | ctrl | 2015 | 5.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | ctrl | 2020 | 5.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | lower | 2020 | 4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | upper | 2020 | 12
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | ctrl | 2030 | 5.1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | ctrl | 2050 | 4.9
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | lower | 2050 | 4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | upper | 2050 | 10
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | ctrl | 2015 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | ctrl | 2020 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | lower | 2020 | 0.2
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | upper | 2020 | 0.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | ctrl | 2030 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | ctrl | 2050 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | lower | 2050 | 0.2
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | upper | 2050 | 0.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | ctrl | 2015 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | ctrl | 2020 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | lower | 2020 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | upper | 2020 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | ctrl | 2030 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | ctrl | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | lower | 2050 | 0.25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | upper | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  | 12 | ctrl | 2015 | 0.25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  | 12 | ctrl | 2020 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  | 12 | lower | 2020 | 0.1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  | 12 | upper | 2020 | 0.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  | 12 | ctrl | 2030 | 0.35
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  | 12 | ctrl | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  | 12 | lower | 2050 | 0.25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  | 12 | upper | 2050 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 12, 13] | ctrl | 2015 | 0.25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 12, 13] | ctrl | 2020 | 0.3
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 12, 13] | lower | 2020 | 0.2
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 12, 13] | upper | 2020 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 12, 13] | ctrl | 2030 | 0.4
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 12, 13] | ctrl | 2050 | 0.5
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 12, 13] | lower | 2050 | 0.25
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 12, 13] | upper | 2050 | 1
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | ctrl | 2015 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | ctrl | 2020 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | lower | 2020 | 0.015
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | upper | 2020 | 0.15
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | ctrl | 2030 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | ctrl | 2050 | 0.05
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | lower | 2050 | 0.015
06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | upper | 2050 | 0.15
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | ctrl | 2015 | 0.82
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | ctrl | 2020 | 0.86
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | lower | 2020 | 0.59
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | upper | 2020 | 0.96
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | ctrl | 2030 | 0.92
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | ctrl | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | lower | 2050 | 0.75
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  | [3, 4, 7] | upper | 2050 | 1.1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | ctrl | 2015 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | ctrl | 2020 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | lower | 2020 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | upper | 2020 | 1.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | ctrl | 2030 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | ctrl | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | lower | 2050 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | [3, 6] | upper | 2050 | 1.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | ctrl | 2015
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | ctrl | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | lower | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | upper | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | ctrl | 2030
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | ctrl | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | lower | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | G |  | upper | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | ctrl | 2015 | 0.42
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | ctrl | 2020 | 0.43
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | lower | 2020 | 0.38
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | upper | 2020 | 0.44
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | ctrl | 2030 | 0.45
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | ctrl | 2050 | 0.47
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | lower | 2050 | 0.42
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | [3, 4] | upper | 2050 | 0.48
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | ctrl | 2015 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | ctrl | 2020 | 0.41
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | lower | 2020 | 0.36
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | upper | 2020 | 0.42
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | ctrl | 2030 | 0.43
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | ctrl | 2050 | 0.45
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | lower | 2050 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 4, 7] | upper | 2050 | 0.46
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | ctrl | 2015 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | ctrl | 2020 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | lower | 2020 | 0.02
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | upper | 2020 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | ctrl | 2030 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | ctrl | 2050 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | lower | 2050 | 0.02
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [5, 6] | upper | 2050 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020 | 10
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050 | 10
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | ctrl | 2015 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | ctrl | 2020 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | lower | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | upper | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | ctrl | 2030 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | ctrl | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | lower | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | H | [5, 6] | upper | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.04
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.04
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.035
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.03
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.025
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | ctrl | 2015 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | ctrl | 2020 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | lower | 2020 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | upper | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | ctrl | 2030 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | ctrl | 2050 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | lower | 2050 | 25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [4, 5, 7] | upper | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | ctrl | 2015 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | ctrl | 2020 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | lower | 2020 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | upper | 2020 | 400
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | ctrl | 2030 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | ctrl | 2050 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | lower | 2050 | 300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 4 | upper | 2050 | 400
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J |  | ctrl | 2015 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J |  | ctrl | 2020 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J |  | lower | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J |  | upper | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J |  | ctrl | 2030 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J |  | ctrl | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J |  | lower | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J |  | upper | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | ctrl | 2015 | 100
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | ctrl | 2020 | 100
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | lower | 2020 | 90
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | upper | 2020 | 120
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | ctrl | 2030 | 100
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | ctrl | 2050 | 100
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | lower | 2050 | 90
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 4 | upper | 2050 | 120
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | K | 8 | ctrl | 2015
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | K | 8 | ctrl | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | K | 8 | lower | 2020 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | K | 8 | upper | 2020 | 0.999
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | K | 8 | ctrl | 2030
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | K | 8 | ctrl | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | K | 8 | lower | 2050 | 0
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | K | 8 | upper | 2050 | 0.999
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [3, 5] | ctrl | 2015 | 0.65
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [3, 5] | ctrl | 2020 | 0.6
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [3, 5] | lower | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [3, 5] | upper | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [3, 5] | ctrl | 2030 | 0.55
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [3, 5] | ctrl | 2050 | 0.55
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [3, 5] | lower | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | [3, 5] | upper | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [3, 5] | ctrl | 2015 | 0.35
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [3, 5] | ctrl | 2020 | 0.35
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [3, 5] | lower | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [3, 5] | upper | 2020
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [3, 5] | ctrl | 2030 | 0.35
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [3, 5] | ctrl | 2050 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [3, 5] | lower | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | [3, 5] | upper | 2050
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | ctrl | 2015 | 10000
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | ctrl | 2020 | 9750
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | lower | 2020 | 7000
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | upper | 2020 | 20000
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | ctrl | 2030 | 9300
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | ctrl | 2050 | 8500
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | lower | 2050 | 6000
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | F | 5 | upper | 2050 | 15000
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | ctrl | 2015 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | ctrl | 2020 | 0.95
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | lower | 2020 | 0.8
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | upper | 2020 | 1.2
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | ctrl | 2030 | 0.9
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | ctrl | 2050 | 0.85
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | lower | 2050 | 0.8
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | upper | 2050 | 1.2
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | ctrl | 2015 | 8
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | ctrl | 2020 | 7.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | lower | 2020 | 6
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | upper | 2020 | 13
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | ctrl | 2030 | 7
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | ctrl | 2050 | 6
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | lower | 2050 | 4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | F | [3, 5, 11] | upper | 2050 | 12
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | ctrl | 2015 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | ctrl | 2020 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | lower | 2020 | 0.2
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | upper | 2020 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | ctrl | 2030 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | ctrl | 2050 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | lower | 2050 | 0.2
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [6, 10] | upper | 2050 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | ctrl | 2015 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | ctrl | 2020 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | lower | 2020 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | upper | 2020 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | ctrl | 2030 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | ctrl | 2050 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | lower | 2050 | 0.25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 6 | upper | 2050 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J | 8 | ctrl | 2015 | 0.25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J | 8 | ctrl | 2020 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J | 8 | lower | 2020 | 0.1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J | 8 | upper | 2020 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J | 8 | ctrl | 2030 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J | 8 | ctrl | 2050 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J | 8 | lower | 2050 | 0.25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | J | 8 | upper | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 8, 13] | ctrl | 2015 | 0.25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 8, 13] | ctrl | 2020 | 0.3
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 8, 13] | lower | 2020 | 0.2
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 8, 13] | upper | 2020 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 8, 13] | ctrl | 2030 | 0.4
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 8, 13] | ctrl | 2050 | 0.5
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 8, 13] | lower | 2050 | 0.25
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C | [6, 8, 13] | upper | 2050 | 1
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | ctrl | 2015 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | ctrl | 2020 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | lower | 2020 | 0.015
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | upper | 2020 | 0.15
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | ctrl | 2030 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | ctrl | 2050 | 0.05
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | lower | 2050 | 0.015
06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | C | [6, 10] | upper | 2050 | 0.15
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2015 | 0.029099
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2020 | 0.029099
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | lower | 2020 | 0.021471
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | upper | 2020 | 0.031962
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2030 | 0.029215
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2050 | 0.02911
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | lower | 2050 | 0.017177
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | upper | 2050 | 0.032382
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2015 | 0.29787
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2020 | 0.29787
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2020 | 0.27028
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2020 | 0.32472
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2030 | 0.30618
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2050 | 0.3187
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2050 | 0.27267
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2050 | 0.35201
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 2.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 3.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 3.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2015 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2030 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2015 | 0.22357
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2020 | 0.22357
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2020 | 0.19
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2020 | 0.25
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2030 | 0.22886
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2050 | 0.23712
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2050 | 0.19
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2050 | 0.27
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2015 | 0.23534
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2020 | 0.23534
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | lower | 2020 | 0.21
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | upper | 2020 | 0.26
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2030 | 0.24091
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2050 | 0.2496
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | lower | 2050 | 0.21
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | upper | 2050 | 0.28
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2015 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2020 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | lower | 2020 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | upper | 2020 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2030 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2050 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | lower | 2050 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | upper | 2050 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2015 | 51.7747
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2020 | 51.7747
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2020 | 46.9803
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2020 | 56.4429
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2030 | 52.9998
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2050 | 54.9114
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2050 | 46.9803
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2050 | 60.6511
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2015 | 2.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2020 | 2.3775
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | lower | 2020 | 2.0209
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | upper | 2020 | 2.7341
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2030 | 2.1501
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2050 | 1.7586
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | lower | 2050 | 1.319
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | upper | 2050 | 2.1983
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2015 | 0.77258
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2020 | 0.77258
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2020 | 0.65669
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2020 | 0.88847
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2030 | 0.75472
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2050 | 0.72845
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2050 | 0.54633
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2050 | 0.91056
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | lower | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | upper | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | lower | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | upper | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | lower | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | upper | 2020 | 3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2030 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | lower | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 20
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 10
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | lower | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | upper | 2020 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | lower | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2015 | 0.99792
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2020 | 0.99792
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | lower | 2020 | 0.98962
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | upper | 2020 | 0.99896
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2030 | 0.99792
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2050 | 0.99792
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | lower | 2050 | 0.99481
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | upper | 2050 | 0.99896
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2015 | 4.794
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 4.6754
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | lower | 2020 | 3.9741
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | upper | 2020 | 5.5502
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2030 | 4.5135
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2050 | 3.9564
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | lower | 2050 | 2.8446
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | upper | 2050 | 4.9046
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2015 | 3.1585
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2020 | 3.0803
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | lower | 2020 | 2.6183
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | upper | 2020 | 3.5424
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2030 | 2.862
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2050 | 2.4989
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | lower | 2050 | 1.8742
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | upper | 2050 | 3.1236
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2015 | 229000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2020 | 186000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | lower | 2020 | 158000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | upper | 2020 | 218000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2030 | 174000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2050 | 148000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | lower | 2050 | 109000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | upper | 2050 | 184000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2015 | 7.9525
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 7.7557
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | lower | 2020 | 6.5923
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | upper | 2020 | 9.0926
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2030 | 7.3755
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2050 | 6.4553
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | lower | 2050 | 4.7188
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | upper | 2050 | 8.0283
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2015 | 24.991
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2020 | 24.991
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | lower | 2020 | 21.2641
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | upper | 2020 | 28.8025
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2030 | 24.427
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2050 | 23.5998
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | lower | 2050 | 17.7371
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | upper | 2050 | 29.4858
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2015 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2020 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | lower | 2020 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | upper | 2020 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2030 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2050 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | lower | 2050 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | upper | 2050 | 2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2015 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2020 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | lower | 2020 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | upper | 2020 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2030 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2050 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | lower | 2050 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | upper | 2050 | 0.2
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2015 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2020 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | lower | 2020 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | upper | 2020 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2030 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2050 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | lower | 2050 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | upper | 2050 | 0.05
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2015 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | lower | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | upper | 2020 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2030 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | lower | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | upper | 2050 | 0.1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2015 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2020 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | lower | 2020 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | upper | 2020 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2030 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2050 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | lower | 2050 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | upper | 2050 | 0.5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2015 | 1.1282
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2020 | 1.1003
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | lower | 2020 | 0.93525
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | upper | 2020 | 1.3062
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2030 | 1.0873
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2050 | 0.98752
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | lower | 2050 | 0.71001
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | upper | 2050 | 1.2242
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2015 | 0.74333
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2020 | 0.72493
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | lower | 2020 | 0.61619
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | upper | 2020 | 0.83367
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2030 | 0.68949
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2050 | 0.62372
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | lower | 2050 | 0.46779
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | upper | 2050 | 0.77965
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2015 | 0.041506
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2020 | 0.041506
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | lower | 2020 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | upper | 2020 | 0.06
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2030 | 0.040149
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2050 | 0.037398
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | lower | 2050 | 0.01
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | upper | 2050 | 0.06
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2015 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | lower | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2030 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | lower | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2015 | 54000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2020 | 43900
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | lower | 2020 | 37300
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | upper | 2020 | 51300
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2030 | 41900
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2050 | 37000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | lower | 2050 | 27100
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | upper | 2050 | 46000
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2015 | 19.8682
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2020 | 16.1483
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | lower | 2020 | 13.726
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | upper | 2020 | 18.8713
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2030 | 15.4302
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2050 | 13.6148
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | lower | 2050 | 9.9855
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | upper | 2050 | 16.9433
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2015 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | lower | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2030 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | lower | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2015 | 0.80185
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2020 | 0.80185
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2020 | 0.76
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2020 | 0.85
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2030 | 0.79888
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2050 | 0.79566
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2050 | 0.73
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2050 | 0.87
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2015 | 0.79009
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2020 | 0.79009
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | lower | 2020 | 0.74
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | upper | 2020 | 0.84
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2030 | 0.78683
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2050 | 0.78318
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | lower | 2050 | 0.71
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | upper | 2050 | 0.86
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2015 | 74.6885
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2020 | 74.6885
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | lower | 2020 | 74.6885
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | upper | 2020 | 74.6885
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2030 | 74.6885
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2050 | 74.6885
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | lower | 2050 | 74.6885
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | upper | 2050 | 74.6885
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2015 | 1.8715
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2020 | 1.8252
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | lower | 2020 | 1.5514
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | upper | 2020 | 2.1398
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2030 | 1.7768
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2050 | 1.6112
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | lower | 2050 | 1.1778
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | upper | 2050 | 2.0038
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2015 | 690
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2020 | 670
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | lower | 2020 | 570
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | upper | 2020 | 790
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2030 | 650
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2050 | 590
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | lower | 2050 | 430
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | upper | 2050 | 740
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.10999
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.10999
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.098605
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.14127
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.11329
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.11906
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.098605
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.14535
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2015 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | lower | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | upper | 2020 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2030 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | lower | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | upper | 2050 | 0
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2015 | 5.88
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2020 | 5.88
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | lower | 2020 | 5
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | upper | 2020 | 6.78
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2030 | 5.88
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2050 | 5.89
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | lower | 2050 | 4.43
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | upper | 2050 | 7.36
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2015 | 17.324
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2020 | 17.324
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | lower | 2020 | 14.7404
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | upper | 2020 | 19.9661
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2030 | 17.3337
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2050 | 17.3507
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | lower | 2050 | 13.0404
08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | upper | 2050 | 21.6781
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2015 | 0.029566
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2020 | 0.029566
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | lower | 2020 | 0.021847
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | upper | 2020 | 0.032244
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2030 | 0.029667
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2050 | 0.029534
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | lower | 2050 | 0.017478
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | upper | 2050 | 0.032647
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [A, B] |  | ctrl | 2015 | 0.28264
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [A, B] |  | ctrl | 2020 | 0.28264
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [A, B] |  | lower | 2020 | 0.25393
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [A, B] |  | upper | 2020 | 0.31158
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [A, B] |  | ctrl | 2030 | 0.29176
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [A, B] |  | ctrl | 2050 | 0.30345
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [A, B] |  | lower | 2050 | 0.25451
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [A, B] |  | upper | 2050 | 0.33817
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 2.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 3.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 3.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | [A, B] |  | ctrl | 2015 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | [A, B] |  | ctrl | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | [A, B] |  | lower | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | [A, B] |  | upper | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | [A, B] |  | ctrl | 2030 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | [A, B] |  | ctrl | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | [A, B] |  | lower | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | [A, B] |  | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2015 | 0.20215
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2020 | 0.20215
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2020 | 0.17
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2020 | 0.23
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2030 | 0.20813
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2050 | 0.21654
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2050 | 0.17
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2050 | 0.25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2015 | 0.21279
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2020 | 0.21279
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | lower | 2020 | 0.19
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | upper | 2020 | 0.24
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2030 | 0.21908
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2050 | 0.22793
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | lower | 2050 | 0.19
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B] |  | upper | 2050 | 0.26
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2015 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2020 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | lower | 2020 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | upper | 2020 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2030 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2050 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | lower | 2050 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | upper | 2050 | 0.01
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2015 | 46.8131
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2020 | 46.8131
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2020 | 42.0581
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2020 | 51.6062
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2030 | 48.1977
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2050 | 50.1453
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2050 | 42.0581
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2050 | 55.8832
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2015 | 2.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2020 | 2.3775
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | lower | 2020 | 2.0209
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | upper | 2020 | 2.7341
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2030 | 2.1501
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2050 | 1.7586
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | lower | 2050 | 1.319
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | upper | 2050 | 2.1983
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2015 | 0.85446
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2020 | 0.85446
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2020 | 0.72629
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2020 | 0.98263
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2030 | 0.82992
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2050 | 0.79768
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2050 | 0.59826
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2050 | 0.9971
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | lower | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | upper | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | lower | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | upper | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | lower | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | upper | 2020 | 3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2030 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | lower | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 20
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 10
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | lower | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | upper | 2020 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | lower | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2015 | 0.99792
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2020 | 0.99792
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | lower | 2020 | 0.98962
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | upper | 2020 | 0.99896
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2030 | 0.99792
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2050 | 0.99792
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | lower | 2050 | 0.99481
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | upper | 2050 | 0.99896
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2015 | 5.3021
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 5.1709
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | lower | 2020 | 4.3952
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | upper | 2020 | 6.1384
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2030 | 4.9632
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2050 | 4.3325
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | lower | 2050 | 3.115
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | upper | 2050 | 5.3708
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2015 | 3.4933
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2020 | 3.4068
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | lower | 2020 | 2.8958
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | upper | 2020 | 3.9178
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2030 | 3.1472
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2050 | 2.7364
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | lower | 2050 | 2.0523
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | upper | 2050 | 3.4205
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2015 | 254000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2020 | 206000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | lower | 2020 | 175000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | upper | 2020 | 241000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2030 | 191000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2050 | 162000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | lower | 2050 | 119000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | upper | 2050 | 202000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2015 | 8.7954
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 8.5777
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | lower | 2020 | 7.291
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | upper | 2020 | 10.0563
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2030 | 8.1104
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2050 | 7.0689
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | lower | 2050 | 5.1673
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | upper | 2050 | 8.7913
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2015 | 27.2767
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2020 | 27.2767
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | lower | 2020 | 23.1118
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | upper | 2020 | 31.6963
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2030 | 26.5199
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2050 | 25.5378
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | lower | 2050 | 19.0439
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | upper | 2050 | 32.151
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2015 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2020 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | lower | 2020 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | upper | 2020 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2030 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2050 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | lower | 2050 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | upper | 2050 | 2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2015 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2020 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | lower | 2020 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | upper | 2020 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2030 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2050 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | lower | 2050 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | upper | 2050 | 0.2
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2015 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2020 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | lower | 2020 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | upper | 2020 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2030 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2050 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | lower | 2050 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | upper | 2050 | 0.05
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2015 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | lower | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | upper | 2020 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2030 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | lower | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | upper | 2050 | 0.1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2015 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2020 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | lower | 2020 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | upper | 2020 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2030 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2050 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | lower | 2050 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | upper | 2050 | 0.5
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2015 | 1.1282
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2020 | 1.1003
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | lower | 2020 | 0.93525
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | upper | 2020 | 1.3062
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2030 | 1.0873
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2050 | 0.98752
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | lower | 2050 | 0.71001
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | upper | 2050 | 1.2242
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2015 | 0.74333
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2020 | 0.72493
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | lower | 2020 | 0.61619
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | upper | 2020 | 0.83367
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2030 | 0.68949
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2050 | 0.62372
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | lower | 2050 | 0.46779
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | upper | 2050 | 0.77965
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2015 | 0.10038
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2020 | 0.10038
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | lower | 2020 | 0.04
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | upper | 2020 | 0.12
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2030 | 0.097086
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2050 | 0.090423
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | lower | 2050 | 0.04
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | upper | 2050 | 0.12
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2015 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | lower | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2030 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | lower | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2015 | 54000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2020 | 43900
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | lower | 2020 | 37300
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | upper | 2020 | 51300
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2030 | 41900
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2050 | 37000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | lower | 2050 | 27100
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | upper | 2050 | 46000
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2015 | 19.8682
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2020 | 16.1483
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | lower | 2020 | 13.726
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | upper | 2020 | 18.8713
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2030 | 15.4302
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2050 | 13.6148
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | lower | 2050 | 9.9855
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | upper | 2050 | 16.9433
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2015 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | lower | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2030 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | lower | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2015 | 0.76349
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2020 | 0.76349
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2020 | 0.72
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2020 | 0.85
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2030 | 0.76185
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2050 | 0.76254
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2050 | 0.7
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2050 | 0.86
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2015 | 0.75285
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2020 | 0.75285
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | lower | 2020 | 0.7
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | upper | 2020 | 0.84
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2030 | 0.7509
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2050 | 0.75114
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | lower | 2050 | 0.68
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | upper | 2050 | 0.85
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2015 | 74.6885
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2020 | 74.6885
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | lower | 2020 | 74.6885
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | upper | 2020 | 74.6885
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2030 | 74.6885
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2050 | 74.6885
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | lower | 2050 | 74.6885
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | upper | 2050 | 74.6885
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2015 | 1.8715
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2020 | 1.8252
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | lower | 2020 | 1.5514
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | upper | 2020 | 2.1398
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2030 | 1.7768
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2050 | 1.6112
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | lower | 2050 | 1.1778
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | upper | 2050 | 2.0038
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2015 | 690
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2020 | 670
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | lower | 2020 | 570
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | upper | 2020 | 790
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2030 | 650
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2050 | 590
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | lower | 2050 | 430
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | upper | 2050 | 740
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.032747
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.032747
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.012212
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.10746
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.03862
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.049538
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.012212
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.11405
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2015 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | lower | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | upper | 2020 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2030 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | lower | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | upper | 2050 | 0
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2015 | 5.8
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2020 | 5.8
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | lower | 2020 | 4.92
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | upper | 2020 | 6.74
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2030 | 5.81
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2050 | 5.82
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | lower | 2050 | 4.34
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | upper | 2050 | 7.33
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2015 | 17.0965
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2020 | 17.0965
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | lower | 2020 | 14.486
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | upper | 2020 | 19.8665
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2030 | 17.1138
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2050 | 17.1459
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | lower | 2050 | 12.786
08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | upper | 2050 | 21.5859
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2015 | 0.029101
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2020 | 0.029101
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | lower | 2020 | 0.021472
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | upper | 2020 | 0.031965
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2030 | 0.029217
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2050 | 0.029112
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | lower | 2050 | 0.017178
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | upper | 2050 | 0.032684
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2015 | 0.29513
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2020 | 0.29513
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2020 | 0.26813
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2020 | 0.32103
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2030 | 0.30295
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2050 | 0.31481
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2050 | 0.27031
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2050 | 0.34633
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 2.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 2.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 2.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 2.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 1.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2015 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2030 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2015 | 0.221
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2020 | 0.221
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2020 | 0.19
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2020 | 0.25
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2030 | 0.22599
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2050 | 0.23383
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2050 | 0.19
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2050 | 0.26
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2015 | 0.23263
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2020 | 0.23263
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | lower | 2020 | 0.21
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | upper | 2020 | 0.26
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2030 | 0.23788
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2050 | 0.24614
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | lower | 2050 | 0.21
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | upper | 2050 | 0.28
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2015 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2020 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | lower | 2020 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | upper | 2020 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2030 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2050 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | lower | 2050 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | upper | 2050 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2015 | 18.6104
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2020 | 18.6104
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2020 | 16.9079
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2020 | 20.2436
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2030 | 19.0304
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2050 | 19.6913
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2050 | 16.9079
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2050 | 21.6627
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2015 | 3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2020 | 2.853
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | lower | 2020 | 2.425
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | upper | 2020 | 3.2809
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2030 | 2.5802
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2050 | 2.1103
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | lower | 2050 | 1.5828
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | upper | 2050 | 2.6379
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2015 | 1.612
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2020 | 1.612
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2020 | 1.3702
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2020 | 1.8538
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2030 | 1.5764
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2050 | 1.5235
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2050 | 1.1426
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2050 | 1.9044
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | lower | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | upper | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | lower | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | upper | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | lower | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | upper | 2020 | 3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2030 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | lower | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 40
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 10
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | lower | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | upper | 2020 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | lower | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2015 | 0.99792
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2020 | 0.99792
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | lower | 2020 | 0.98962
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | upper | 2020 | 0.99896
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2030 | 0.99792
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2050 | 0.99792
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | lower | 2050 | 0.99481
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | upper | 2050 | 0.99896
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2015 | 5.6232
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 5.484
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | lower | 2020 | 4.6614
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | upper | 2020 | 6.5215
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2030 | 5.311
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2050 | 4.6625
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | lower | 2050 | 3.3445
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | upper | 2050 | 5.7773
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2015 | 3.6271
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2020 | 3.5373
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | lower | 2020 | 3.0067
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | upper | 2020 | 4.0679
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2030 | 3.2901
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2050 | 2.8764
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | lower | 2050 | 2.1573
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | upper | 2050 | 3.5955
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2015 | 298000
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2020 | 262000
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | lower | 2020 | 223000
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | upper | 2020 | 306000
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2030 | 245000
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2050 | 209000
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | lower | 2050 | 154000
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | upper | 2050 | 260000
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2015 | 9.2503
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 9.0213
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | lower | 2020 | 7.6681
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | upper | 2020 | 10.5894
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2030 | 8.6011
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2050 | 7.5389
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | lower | 2050 | 5.5018
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | upper | 2050 | 9.3728
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2015 | 25.2821
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2020 | 25.2821
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | lower | 2020 | 21.5118
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | upper | 2020 | 29.138
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2030 | 24.7381
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2050 | 23.9312
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | lower | 2050 | 17.9863
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | upper | 2050 | 29.8916
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2015 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2020 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | lower | 2020 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | upper | 2020 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2030 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2050 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | lower | 2050 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | upper | 2050 | 2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2015 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2020 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | lower | 2020 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | upper | 2020 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2030 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2050 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | lower | 2050 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | upper | 2050 | 0.2
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2015 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2020 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | lower | 2020 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | upper | 2020 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2030 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2050 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | lower | 2050 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | upper | 2050 | 0.05
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2015 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | lower | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | upper | 2020 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2030 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | lower | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | upper | 2050 | 0.1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2015 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2020 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | lower | 2020 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | upper | 2020 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2030 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2050 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | lower | 2050 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | upper | 2050 | 0.5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2015 | 1.3081
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2020 | 1.2757
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | lower | 2020 | 1.0844
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | upper | 2020 | 1.5171
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2030 | 1.2634
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2050 | 1.1476
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | lower | 2050 | 0.82322
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | upper | 2050 | 1.422
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2015 | 0.84377
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2020 | 0.82288
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | lower | 2020 | 0.69945
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | upper | 2020 | 0.94631
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2030 | 0.78265
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2050 | 0.70799
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | lower | 2050 | 0.531
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | upper | 2050 | 0.88499
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2015 | 0.041506
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2020 | 0.041506
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | lower | 2020 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | upper | 2020 | 0.06
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2030 | 0.040149
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2050 | 0.037398
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | lower | 2050 | 0.01
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | upper | 2050 | 0.06
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, P] |  | ctrl | 2015 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, P] |  | ctrl | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, P] |  | lower | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, P] |  | upper | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, P] |  | ctrl | 2030 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, P] |  | ctrl | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, P] |  | lower | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, P] |  | upper | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2015 | 69300
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2020 | 61000
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | lower | 2020 | 51900
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | upper | 2020 | 71200
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2030 | 58200
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2050 | 51400
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | lower | 2050 | 37800
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | upper | 2050 | 64000
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2015 | 25.5114
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2020 | 22.4605
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | lower | 2020 | 19.0915
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | upper | 2020 | 26.1978
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2030 | 21.4186
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2050 | 18.9197
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | lower | 2050 | 13.9136
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | upper | 2050 | 23.5576
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, P] |  | ctrl | 2015 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, P] |  | ctrl | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, P] |  | lower | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, P] |  | upper | 2020 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, P] |  | ctrl | 2030 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, P] |  | ctrl | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, P] |  | lower | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, P] |  | upper | 2050 | 1
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2015 | 0.79986
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2020 | 0.79986
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2020 | 0.76
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2020 | 0.85
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2030 | 0.79711
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2050 | 0.79418
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2050 | 0.73
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2050 | 0.88
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2015 | 0.78823
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2020 | 0.78823
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | lower | 2020 | 0.74
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | upper | 2020 | 0.84
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2030 | 0.78521
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2050 | 0.78187
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | lower | 2050 | 0.71
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | upper | 2050 | 0.86
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2015 | 27.1594
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2020 | 27.1594
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | lower | 2020 | 27.1594
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | upper | 2020 | 27.1594
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2030 | 27.1594
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2050 | 27.1594
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | lower | 2050 | 27.1594
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | upper | 2050 | 27.1594
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2015 | 2.1519
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2020 | 2.0986
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | lower | 2020 | 1.7838
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | upper | 2020 | 2.4634
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2030 | 2.046
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2050 | 1.8556
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | lower | 2050 | 1.3542
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | upper | 2050 | 2.307
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2015 | 790
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2020 | 770
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | lower | 2020 | 660
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | upper | 2020 | 910
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2030 | 750
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2050 | 680
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | lower | 2050 | 500
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | upper | 2050 | 850
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.11001
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.11001
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.098624
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.14129
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.11331
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.11907
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.098624
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.14332
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | P |  | ctrl | 2015 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | P |  | ctrl | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | P |  | lower | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | P |  | upper | 2020 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | P |  | ctrl | 2030 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | P |  | ctrl | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | P |  | lower | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | P |  | upper | 2050 | 0
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2015 | 5.88
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2020 | 5.88
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | lower | 2020 | 5
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | upper | 2020 | 6.78
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2030 | 5.88
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2050 | 5.89
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | lower | 2050 | 4.43
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | upper | 2050 | 7.36
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2015 | 17.324
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2020 | 17.324
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | lower | 2020 | 14.7405
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | upper | 2020 | 19.9662
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2030 | 17.3338
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2050 | 17.3507
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | lower | 2050 | 13.0405
08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | upper | 2050 | 21.6721
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2015 | 0.029099
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2020 | 0.029099
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | lower | 2020 | 0.021471
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | upper | 2020 | 0.032286
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2030 | 0.029216
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | ctrl | 2050 | 0.029389
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | lower | 2050 | 0.017177
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B] |  | upper | 2050 | 0.032998
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2015 | 0.28712
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2020 | 0.28712
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2020 | 0.26149
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2020 | 0.31105
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2030 | 0.29381
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2050 | 0.30055
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2050 | 0.26103
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2050 | 0.33093
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 2.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 2.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 2.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 2.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 1.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2015 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2030 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | ctrl | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | lower | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | [A, B] |  | upper | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2015 | 0.21592
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2020 | 0.21592
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2020 | 0.18
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2020 | 0.24
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2030 | 0.2203
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2050 | 0.22643
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2050 | 0.18
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2050 | 0.25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2015 | 0.22729
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2020 | 0.22729
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | lower | 2020 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | upper | 2020 | 0.25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2030 | 0.23189
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2050 | 0.23834
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | lower | 2050 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, B, C] |  | upper | 2050 | 0.27
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2015 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2020 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | lower | 2020 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | upper | 2020 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2030 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2050 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | lower | 2050 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | upper | 2050 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2015 | 7.9551
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2020 | 7.9551
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2020 | 7.2451
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2020 | 8.6182
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2030 | 8.1163
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | ctrl | 2050 | 8.342
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | lower | 2050 | 7.2451
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | [A, B] |  | upper | 2050 | 9.1851
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2015 | 3.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2020 | 3.3285
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | lower | 2020 | 2.8292
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | upper | 2020 | 3.8277
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2030 | 3.0102
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2050 | 2.4621
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | lower | 2050 | 1.8466
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | upper | 2050 | 3.0776
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2015 | 2.5141
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2020 | 2.5141
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2020 | 2.137
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2020 | 2.8912
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2030 | 2.4642
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2050 | 2.3975
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2050 | 1.7981
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2050 | 2.9969
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | lower | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | upper | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | lower | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | upper | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | lower | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | upper | 2020 | 3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2030 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | lower | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 40
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 20
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | lower | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | upper | 2020 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | lower | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2015 | 0.99792
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2020 | 0.99792
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | lower | 2020 | 0.98962
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | upper | 2020 | 0.99896
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2030 | 0.99792
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2050 | 0.99792
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | lower | 2050 | 0.99481
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | upper | 2050 | 0.99896
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2015 | 6.6251
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 6.4611
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | lower | 2020 | 5.4919
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | upper | 2020 | 7.6898
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2030 | 6.2775
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | ctrl | 2050 | 5.5487
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | lower | 2050 | 3.9759
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | N | 1 | upper | 2050 | 6.8739
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2015 | 4.026
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2020 | 3.9264
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | lower | 2020 | 3.3374
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | upper | 2020 | 4.5153
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2030 | 3.6602
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | ctrl | 2050 | 3.2215
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | lower | 2050 | 2.4161
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 1 | upper | 2050 | 4.0269
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2015 | 425000
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2020 | 411000
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | lower | 2020 | 349000
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | upper | 2020 | 478000
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2030 | 382000
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | ctrl | 2050 | 328000
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | lower | 2050 | 242000
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | L | 1 | upper | 2050 | 408000
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2015 | 10.6511
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 10.3874
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | lower | 2020 | 8.8293
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | upper | 2020 | 12.2051
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2030 | 9.9377
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2050 | 8.7701
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | lower | 2050 | 6.392
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | upper | 2050 | 10.9008
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2015 | 25.8766
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2020 | 25.8766
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | lower | 2020 | 22.0177
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | upper | 2020 | 29.8137
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2030 | 25.3769
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | ctrl | 2050 | 24.7023
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | lower | 2050 | 18.5749
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | K | 1 | upper | 2050 | 30.8609
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2015 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2020 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | lower | 2020 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | upper | 2020 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2030 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | ctrl | 2050 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | lower | 2050 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [F, G] |  | upper | 2050 | 2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2015 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2020 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | lower | 2020 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | upper | 2020 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2030 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | ctrl | 2050 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | lower | 2050 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [F, G] |  | upper | 2050 | 0.2
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2015
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2020
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | lower | 2020
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | upper | 2020
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2030
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | ctrl | 2050
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | lower | 2050
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | F |  | upper | 2050
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2015 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | lower | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | upper | 2020 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2030 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | ctrl | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | lower | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | [F, G] |  | upper | 2050 | 0.1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2015 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2020 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | lower | 2020 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | upper | 2020 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2030 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | ctrl | 2050 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | lower | 2050 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [F, G] |  | upper | 2050 | 0.5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2015 | 1.9022
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2020 | 1.4685
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | lower | 2020 | 1.2482
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | upper | 2020 | 1.7478
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2030 | 1.4557
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2050 | 1.3225
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | lower | 2050 | 0.94762
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | upper | 2050 | 1.6384
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2015 | 1.1559
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2020 | 0.89242
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | lower | 2020 | 0.75855
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | upper | 2020 | 1.0263
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2030 | 0.84879
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2050 | 0.76782
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | lower | 2050 | 0.57587
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | upper | 2050 | 0.95978
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2015 | 0.041506
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2020 | 0.041506
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | lower | 2020 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | upper | 2020 | 0.06
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2030 | 0.040149
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2050 | 0.038774
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | lower | 2050 | 0.01
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | upper | 2050 | 0.06
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2015 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | lower | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2030 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | lower | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2015 | 96500
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2020 | 93400
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | lower | 2020 | 79400
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | upper | 2020 | 108500
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2030 | 88600
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2050 | 78100
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | lower | 2050 | 57700
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | upper | 2050 | 97300
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2015 | 35.5467
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2020 | 34.3726
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | lower | 2020 | 29.2167
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | upper | 2020 | 39.9629
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2030 | 32.6072
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2050 | 28.7411
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | lower | 2050 | 21.23
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | upper | 2050 | 35.8178
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2015 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | lower | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | upper | 2020 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2030 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | lower | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | upper | 2050 | 1
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2015 | 0.80299
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2020 | 0.80299
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2020 | 0.77
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2020 | 0.86
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2030 | 0.80087
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2050 | 0.80493
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2050 | 0.74
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2050 | 0.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2015 | 0.79162
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2020 | 0.79162
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | lower | 2020 | 0.75
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | upper | 2020 | 0.85
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2030 | 0.78927
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | ctrl | 2050 | 0.79302
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | lower | 2050 | 0.72
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B] |  | upper | 2050 | 0.86
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2015 | 11.8823
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2020 | 11.8823
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | lower | 2020 | 11.8823
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | upper | 2020 | 11.8823
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2030 | 11.8823
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2050 | 11.8823
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | lower | 2050 | 11.8823
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | upper | 2050 | 11.8823
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2015 | 2.4209
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2020 | 2.3609
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | lower | 2020 | 2.0068
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | upper | 2020 | 2.7741
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2030 | 2.3045
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2050 | 2.0903
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | lower | 2050 | 1.5235
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | upper | 2050 | 2.5981
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2015 | 890
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2020 | 870
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | lower | 2020 | 740
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | upper | 2020 | 1020
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2030 | 850
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2050 | 770
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | lower | 2050 | 560
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | upper | 2050 | 960
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.11006
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.11006
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.098681
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.13921
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.11336
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.11625
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.098681
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.14126
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2015 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | lower | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | upper | 2020 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2030 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | ctrl | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | lower | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | O |  | upper | 2050 | 0
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2015 | 5.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2020 | 5.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | lower | 2020 | 5
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | upper | 2020 | 6.78
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2030 | 5.88
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2050 | 5.89
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | lower | 2050 | 4.43
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | upper | 2050 | 7.36
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2015 | 17.3242
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2020 | 17.3242
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | lower | 2020 | 14.7407
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | upper | 2020 | 19.96
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2030 | 17.3339
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2050 | 17.3424
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | lower | 2050 | 13.0407
08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | upper | 2050 | 21.6661
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B, C] |  | ctrl | 2015 | 0.025848
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B, C] |  | ctrl | 2020 | 0.025848
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B, C] |  | lower | 2020 | 0.019033
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B, C] |  | upper | 2020 | 0.027727
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B, C] |  | ctrl | 2030 | 0.025501
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B, C] |  | ctrl | 2050 | 0.024842
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B, C] |  | lower | 2050 | 0.014903
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [A, B, C] |  | upper | 2050 | 0.027608
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 2
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 2
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 1.5
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 2.5
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 2
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 2
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 1.5
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 2.5
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2015 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | lower | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | upper | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2030 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | lower | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | upper | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, B] |  | ctrl | 2015 | 36.9496
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, B] |  | ctrl | 2020 | 36.9496
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, B] |  | lower | 2020 | 36.2641
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, B] |  | upper | 2020 | 37.9162
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, B] |  | ctrl | 2030 | 37.0376
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, B] |  | ctrl | 2050 | 37.2147
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, B] |  | lower | 2050 | 36.2641
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, B] |  | upper | 2050 | 38.0804
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2015 | 3
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2020 | 2.853
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | lower | 2020 | 2.425
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | upper | 2020 | 3.2809
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2030 | 2.5802
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | ctrl | 2050 | 2.1103
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | lower | 2050 | 1.5828
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | E | 1 | upper | 2050 | 2.6379
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | 1 | ctrl | 2015 | 0.54128
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | 1 | ctrl | 2020 | 0.54128
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | 1 | lower | 2020 | 0.46009
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | 1 | upper | 2020 | 0.62247
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | 1 | ctrl | 2030 | 0.53999
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | 1 | ctrl | 2050 | 0.53742
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | 1 | lower | 2050 | 0.40307
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | 1 | upper | 2050 | 0.67178
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2015 | 1.0557
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2020 | 1.0557
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2020 | 1.03
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2020 | 1.09
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2030 | 1.0582
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | ctrl | 2050 | 1.0633
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | lower | 2050 | 1.03
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, B, C] |  | upper | 2050 | 1.09
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2015 | 1.0557
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2020 | 1.0557
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, C] |  | lower | 2020 | 1.03
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, C] |  | upper | 2020 | 1.09
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2030 | 1.0582
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, C] |  | ctrl | 2050 | 1.0633
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, C] |  | lower | 2050 | 1.03
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, C] |  | upper | 2050 | 1.09
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2015 | 0.3
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2020 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | lower | 2020 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | upper | 2020 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2030 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | ctrl | 2050 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | lower | 2050 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 2 | upper | 2050 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2015 | 1.2
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | lower | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | upper | 2020 | 3
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2030 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | ctrl | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | lower | 2050 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2015 | 80
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2020 | 60
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | lower | 2020 | 10
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | upper | 2020 | 60
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2030 | 40
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | ctrl | 2050 | 20
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | lower | 2050 | 10
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | [2, 3, 5] | upper | 2050 | 60
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2015 | 0.3
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2020 | 0.3
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | lower | 2020 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | upper | 2020 | 2
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2030 | 0.3
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | ctrl | 2050 | 0.3
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | lower | 2050 | 0.1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | J | 2 | upper | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2015 | 0.99792
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2020 | 0.99792
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | lower | 2020 | 0.98962
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | upper | 2020 | 0.99896
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2030 | 0.99792
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | ctrl | 2050 | 0.99792
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | lower | 2050 | 0.99481
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | H | 1 | upper | 2050 | 0.99896
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | P |  | ctrl | 2015 | 1.0239
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | P |  | ctrl | 2020 | 0.99858
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | P |  | lower | 2020 | 0.87034
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | P |  | upper | 2020 | 1.2334
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | P |  | ctrl | 2030 | 1.0033
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | P |  | ctrl | 2050 | 0.90852
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | P |  | lower | 2050 | 0.70725
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | P |  | upper | 2050 | 1.2342
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | P |  | ctrl | 2015 | 0.76008
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | P |  | ctrl | 2020 | 0.74127
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | P |  | lower | 2020 | 0.64607
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | P |  | upper | 2020 | 0.87409
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | P |  | ctrl | 2030 | 0.70335
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | P |  | ctrl | 2050 | 0.63323
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | P |  | lower | 2050 | 0.525
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | P |  | upper | 2050 | 0.87501
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2015 | 1.6284
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2020 | 1.7835
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [K, P] |  | lower | 2020 | 1.6747
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [K, P] |  | upper | 2020 | 1.8185
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2030 | 2.5756
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2050 | 2.9065
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [K, P] |  | lower | 2050 | 2.7674
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [K, P] |  | upper | 2050 | 3.0835
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2015 | 5.5938
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2020 | 5.5938
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [K, P] |  | lower | 2020 | 4.6408
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [K, P] |  | upper | 2020 | 6.5657
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2030 | 5.5834
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2050 | 5.5624
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [K, P] |  | lower | 2050 | 4.0904
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [K, P] |  | upper | 2050 | 7.1268
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | P |  | ctrl | 2015 | 80700
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | P |  | ctrl | 2020 | 78000
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | P |  | lower | 2020 | 66800
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | P |  | upper | 2020 | 91500
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | P |  | ctrl | 2030 | 73900
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | P |  | ctrl | 2050 | 64700
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | P |  | lower | 2050 | 49400
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | P |  | upper | 2050 | 83500
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | P |  | ctrl | 2015 | 1.784
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | P |  | ctrl | 2020 | 1.7399
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | P |  | lower | 2020 | 1.5164
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | P |  | upper | 2020 | 2.1075
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | P |  | ctrl | 2030 | 1.7066
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | P |  | ctrl | 2050 | 1.5418
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | P |  | lower | 2050 | 1.2323
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | P |  | upper | 2050 | 2.1092
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2015 | 7.2223
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2020 | 7.3773
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [K, P] |  | lower | 2020 | 6.3156
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [K, P] |  | upper | 2020 | 8.3842
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2030 | 8.159
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [K, P] |  | ctrl | 2050 | 8.4688
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [K, P] |  | lower | 2050 | 6.8578
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [K, P] |  | upper | 2050 | 10.2104
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | G |  | ctrl | 2015 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | G |  | ctrl | 2020 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | G |  | lower | 2020 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | G |  | upper | 2020 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | G |  | ctrl | 2030 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | G |  | ctrl | 2050 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | G |  | lower | 2050 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | G |  | upper | 2050 | 12
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | ctrl | 2015 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | ctrl | 2020 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | lower | 2020 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | upper | 2020 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | ctrl | 2030 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | ctrl | 2050 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | lower | 2050 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | G |  | upper | 2050 | 0.7
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2015 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | lower | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | upper | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2030 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | lower | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | upper | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G |  | ctrl | 2015 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G |  | ctrl | 2020 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G |  | lower | 2020 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G |  | upper | 2020 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G |  | ctrl | 2030 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G |  | ctrl | 2050 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G |  | lower | 2050 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G |  | upper | 2050 | 8
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2015 | 1.081
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2020 | 1.0542
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | lower | 2020 | 0.91882
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | upper | 2020 | 1.3021
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2030 | 1.0617
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | ctrl | 2050 | 0.96601
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | lower | 2050 | 0.752
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | N | 1 | upper | 2050 | 1.3123
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2015 | 0.80242
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2020 | 0.78256
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | lower | 2020 | 0.68206
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | upper | 2020 | 0.92278
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2030 | 0.7443
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | ctrl | 2050 | 0.6733
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | lower | 2050 | 0.55822
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | M | 1 | upper | 2050 | 0.93037
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (electricity cost) [2015-EUR/t_i] | Variable O&M | electricity cost | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2015 | 5.0638
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (electricity cost) [2015-EUR/t_i] | Variable O&M | electricity cost | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2020 | 5.5461
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (electricity cost) [2015-EUR/t_i] | Variable O&M | electricity cost | EUR/t_i | 2015 | K | [1, 4] | lower | 2020 | 5.3441
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (electricity cost) [2015-EUR/t_i] | Variable O&M | electricity cost | EUR/t_i | 2015 | K | [1, 4] | upper | 2020 | 5.5499
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (electricity cost) [2015-EUR/t_i] | Variable O&M | electricity cost | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2030 | 8.0283
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (electricity cost) [2015-EUR/t_i] | Variable O&M | electricity cost | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2050 | 9.103
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (electricity cost) [2015-EUR/t_i] | Variable O&M | electricity cost | EUR/t_i | 2015 | K | [1, 4] | lower | 2050 | 8.869
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (electricity cost) [2015-EUR/t_i] | Variable O&M | electricity cost | EUR/t_i | 2015 | K | [1, 4] | upper | 2050 | 9.4108
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (other O&M) [2015-EUR/t_i] | Variable O&M | other O&M | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2015 | 17.3949
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (other O&M) [2015-EUR/t_i] | Variable O&M | other O&M | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2020 | 17.3949
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (other O&M) [2015-EUR/t_i] | Variable O&M | other O&M | EUR/t_i | 2015 | K | [1, 4] | lower | 2020 | 14.8088
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (other O&M) [2015-EUR/t_i] | Variable O&M | other O&M | EUR/t_i | 2015 | K | [1, 4] | upper | 2020 | 20.0382
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (other O&M) [2015-EUR/t_i] | Variable O&M | other O&M | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2030 | 17.4036
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (other O&M) [2015-EUR/t_i] | Variable O&M | other O&M | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2050 | 17.4211
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (other O&M) [2015-EUR/t_i] | Variable O&M | other O&M | EUR/t_i | 2015 | K | [1, 4] | lower | 2050 | 13.1088
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (other O&M) [2015-EUR/t_i] | Variable O&M | other O&M | EUR/t_i | 2015 | K | [1, 4] | upper | 2050 | 21.7507
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2015 | 0.041506
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2020 | 0.041506
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | lower | 2020 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | upper | 2020 | 0.06
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2030 | 0.040149
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | ctrl | 2050 | 0.037398
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | lower | 2050 | 0.01
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | [A, B, D] |  | upper | 2050 | 0.06
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2015 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2020 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | lower | 2020 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | upper | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2030 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | ctrl | 2050 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | lower | 2050 | 0
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, O] |  | upper | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2015 | 85200
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2020 | 82300
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | lower | 2020 | 70500
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | upper | 2020 | 96600
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2030 | 78200
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | ctrl | 2050 | 68800
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | lower | 2050 | 52600
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | L | 1 | upper | 2050 | 88800
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2015 | 31.3534
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2020 | 30.3043
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | lower | 2020 | 25.9712
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | upper | 2020 | 35.5719
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2030 | 28.7767
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | ctrl | 2050 | 25.3409
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | lower | 2050 | 19.3503
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/t_i/y] | Fixed O&M | *total | EUR/t_i/y | 2015 | L | [1, 4] | upper | 2050 | 32.6849
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2015 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | lower | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | upper | 2020 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2030 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | ctrl | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | lower | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, O] |  | upper | 2050 | 1
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2015 | 11.8823
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2020 | 11.8823
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | lower | 2020 | 11.8823
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | upper | 2020 | 11.8823
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2030 | 11.8823
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | ctrl | 2050 | 11.8823
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | lower | 2050 | 11.8823
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Incineration capacity [t_i/h] | Incineration capacity |  | t_i/h |  | [A, B] |  | upper | 2050 | 11.8823
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2015 | 1.8834
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2020 | 1.8368
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | lower | 2020 | 1.6009
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | upper | 2020 | 2.2249
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2030 | 1.806
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | ctrl | 2050 | 1.6393
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | lower | 2050 | 1.3102
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | N | 1 | upper | 2050 | 2.2427
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2015 | 690
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2020 | 680
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | lower | 2020 | 590
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | upper | 2020 | 820
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2030 | 660
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | ctrl | 2050 | 600
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | lower | 2050 | 480
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/t_i] | Nominal investment | *total | MEUR/t_i | 2015 | N | 1 | upper | 2050 | 830
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2015 | 0.13406
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2020 | 0.13406
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | lower | 2020 | 0.12183
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | upper | 2020 | 0.16575
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2030 | 0.13702
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | ctrl | 2050 | 0.14295
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | lower | 2050 | 0.12183
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, K] |  | upper | 2050 | 0.16999
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2015 | 22.4587
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2020 | 22.9409
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | lower | 2020 | 20.1529
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | upper | 2020 | 25.5882
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2030 | 25.4319
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | ctrl | 2050 | 26.524
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | lower | 2050 | 21.9778
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Output of recovered condensate [2015-EUR/t_i] | Output of recovered condensate |  | EUR/t_i | 2015 | K | [1, 4] | upper | 2050 | 31.1615
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2015 | 7.62
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2020 | 7.79
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | lower | 2020 | 6.84
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | upper | 2020 | 8.69
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2030 | 8.63
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | ctrl | 2050 | 9
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | lower | 2050 | 7.46
08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | K | 1 | upper | 2050 | 10.58
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.029624
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.02941
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.021813
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.032721
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.029426
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.02935
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.017993
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.034321
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2015 | 0.37316
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2020 | 0.37325
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2020 | 0.33993
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2020 | 0.49643
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2030 | 0.37512
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2050 | 0.36611
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2050 | 0.35455
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2050 | 0.5103
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 4.5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 5.5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 4
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 5.5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2015 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2030 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.28855
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.28915
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.24
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.39
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.2902
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.28513
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.26
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.4
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.30373
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.30437
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.27
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.41
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.30547
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.30014
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.29
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.42
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 182.2401
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 182.6228
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 166.3174
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 242.8899
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 183.2811
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 180.083
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 174.3983
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 251.008
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2015 | 0.082309
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2020 | 0.082137
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2020 | 0.069816
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2020 | 0.094457
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2030 | 0.081841
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2050 | 0.083295
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2050 | 0.062471
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2050 | 0.10412
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 8
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 6
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 30
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 20
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 30
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 20
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 10
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 20
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 0.3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2015 | 0.9797
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2020 | 0.9797
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | lower | 2020 | 0.94925
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | upper | 2020 | 0.98985
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2030 | 0.9797
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2050 | 0.9797
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | lower | 2050 | 0.9797
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | upper | 2050 | 0.98985
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 2.1875
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 2.1289
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.7838
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 2.5763
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 2.0176
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 1.9243
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 1.4805
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 2.6336
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.1902
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 1.1584
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.0096
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.3659
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 1.0978
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 1.0107
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 0.83794
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.3966
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015 | 97000
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020 | 95000
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020 | 80000
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020 | 111000
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030 | 89000
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050 | 84000
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050 | 64000
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050 | 110000
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 3.3778
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.2873
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 2.7934
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 3.9422
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 3.1153
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 2.935
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 2.3185
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 4.0301
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 4.3893
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 4.3872
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 3.1053
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 4.9345
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 4.3712
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 4.4502
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 2.7786
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 5.3745
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 12
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.45
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 0.02
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.04
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2015 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2020 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | lower | 2020 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | upper | 2020 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2030 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2050 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | lower | 2050 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | upper | 2050 | 2
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.66443
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.64799
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.54294
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.78415
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.61631
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.57757
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.44436
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.79043
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.36152
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.35257
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.30729
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.41574
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.33533
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.30334
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.2515
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.41916
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.019432
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.018691
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.01
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.28
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.018689
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.018699
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.01
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.28
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 29500
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 28800
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 24300
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 33900
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 27300
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 25100
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 19100
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 32900
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.01
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.0097525
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.0085
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.0115
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.0092757
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.0083909
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.0069568
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.011595
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.82914
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.83067
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.47
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.87
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.8296
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.83481
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.46
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.85
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.81395
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.81545
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.44
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.85
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.81433
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.8198
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.43
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.83
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 1.0259
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 1.0006
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.85023
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 1.1999
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 0.95164
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.88091
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.69586
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 1.2096
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.22132
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.22132
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.22327
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.22124
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.22166
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.22324
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 1
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 1.33
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 1.34
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.95
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 1.5
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 1.34
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 1.34
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.83
09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 1.61
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.029781
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.029563
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.022017
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.032889
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.029578
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.029502
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.018156
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.034488
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015 | 0.34939
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020 | 0.34888
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020 | 0.31567
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020 | 0.47289
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030 | 0.35063
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050 | 0.34231
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050 | 0.3315
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050 | 0.48798
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 4.5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 5.5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 4
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 5.5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2015 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | lower | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | upper | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2030 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | lower | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | upper | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.26842
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.26892
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.23
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.37
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.26991
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.26517
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.24
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.38
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.28255
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.28307
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.39
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.28411
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.27913
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.27
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.4
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 169.5293
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 169.8425
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 153.6782
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 230.2133
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 170.4686
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 167.4763
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 162.187
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 238.7485
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2015 | 0.08848
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2020 | 0.088317
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2020 | 0.07507
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2020 | 0.10156
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2030 | 0.087993
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2050 | 0.089565
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2050 | 0.067174
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2050 | 0.11196
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 8
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 6
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 5
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 30
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 20
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 30
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 20
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 10
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 20
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 0.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2015 | 0.9797
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2020 | 0.9797
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | lower | 2020 | 0.94925
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | upper | 2020 | 0.98985
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2030 | 0.9797
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2050 | 0.9797
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | lower | 2050 | 0.9797
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | upper | 2050 | 0.98985
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 2.3516
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 2.2891
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.918
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 2.7701
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 2.1692
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 2.0692
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 1.592
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 2.8318
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.2795
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 1.2455
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.0856
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.4687
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 1.1803
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 1.0868
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 0.90102
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.5017
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015 | 105000
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020 | 102000
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020 | 86000
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020 | 120000
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030 | 96000
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050 | 90000
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050 | 69000
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050 | 118000
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 3.631
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.5346
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 3.0036
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 4.2388
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 3.3495
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 3.156
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 2.493
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 4.3335
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 4.5977
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 4.6015
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 3.3389
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 5.1899
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 4.5843
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 4.6676
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 2.9877
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 5.6615
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 12
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 0.02
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2015 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2020 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | lower | 2020 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | upper | 2020 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2030 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2050 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | lower | 2050 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | upper | 2050 | 2
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.66443
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.64799
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.54294
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.78415
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.61631
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.57757
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.44436
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.79043
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.36152
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.35257
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.30729
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.41574
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.33533
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.30334
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.2515
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.41916
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.046395
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.044624
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.28
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.04462
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.044641
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.04
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.28
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 29500
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 28800
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 24300
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 33900
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 27300
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 25100
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 19100
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 32900
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.01
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.0097525
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.0085
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.0115
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.0092757
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.0083909
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.0069568
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.011595
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.82282
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.82553
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.48
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.86
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.82451
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.82939
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.48
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.85
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.80869
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.81138
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.46
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.84
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.8103
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.81543
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.45
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.83
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 1.0259
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 1.0006
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.85023
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 1.1999
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 0.95164
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.88091
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.69586
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 1.2096
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.18721
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.18721
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.19047
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.18713
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.18755
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.19044
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 1
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 1.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 1.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.95
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 1.47
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 1.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 1.3
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.83
09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 1.58
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.029611
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.029611
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.021853
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.032707
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.029627
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.029548
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.017985
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.034305
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2015 | 0.36575
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2020 | 0.36575
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2020 | 0.3411
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2020 | 0.48905
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2030 | 0.36768
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2050 | 0.35852
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2050 | 0.34795
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2050 | 0.50089
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 2.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 2.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 2.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 2.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 1.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2015 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2030 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | ctrl | 2015 | 0.28227
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | ctrl | 2020 | 0.28227
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | lower | 2020 | 0.24
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | upper | 2020 | 0.38
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | ctrl | 2030 | 0.28335
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | ctrl | 2050 | 0.27821
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | lower | 2050 | 0.25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | upper | 2050 | 0.39
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2015 | 0.29713
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2020 | 0.29713
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | lower | 2020 | 0.27
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | upper | 2020 | 0.4
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2030 | 0.29826
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2050 | 0.29285
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | lower | 2050 | 0.28
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | upper | 2050 | 0.41
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 23.7703
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 23.7703
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 22.1679
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 31.7831
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 23.8607
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 23.428
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 22.737
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 32.7311
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.21035
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.21035
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.17879
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.2419
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.20955
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.21342
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.16006
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.26677
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 1.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 90
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 60
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 40
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 60
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 40
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 20
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 20
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 40
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2015 | 0.9797
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2020 | 0.9797
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | lower | 2020 | 0.94925
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | upper | 2020 | 0.98985
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2030 | 0.9797
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2050 | 0.9797
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | lower | 2050 | 0.9797
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | upper | 2050 | 0.98985
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 2.4331
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 2.3729
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.9465
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 2.798
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 2.2483
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 2.1738
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 1.6164
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 2.9647
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 1.1703
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.02
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.38
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 1.1089
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 1.0216
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 0.84703
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.4117
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015 | 154000
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020 | 149000
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020 | 126000
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020 | 173000
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030 | 140000
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050 | 129000
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050 | 97000
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050 | 167000
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 3.6331
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.5432
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 2.9666
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 4.1781
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 3.3572
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 3.1955
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 2.4634
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 4.3764
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 4.4872
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 4.4872
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 3.181
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 5.0551
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 4.4699
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 4.5539
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 2.8477
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 5.5085
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 8
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.04
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2015 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | lower | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | upper | 2020 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2030 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2050 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | lower | 2050 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | upper | 2050 | 2
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.72294
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.70504
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.57837
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.83138
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.67057
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.63661
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.47336
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.86822
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.35656
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.34774
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.30308
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.41005
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.33074
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.29919
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.24805
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.41342
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.019432
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.019432
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.01
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.26
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.01943
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.01944
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.01
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.28
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 45800
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 44400
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 37300
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 51500
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 41800
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 37800
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 28300
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 48800
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.015
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.014629
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.01275
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.01725
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.013914
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.012586
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.010435
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.017392
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.82723
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.82723
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.49
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.86
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.82611
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.83147
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.46
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.85
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.81237
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.81237
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.46
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.84
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.81119
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.81683
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.43
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.83
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 1.0795
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 1.0528
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.88145
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 1.2414
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 1.0013
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.9358
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.72142
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 1.2816
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.22132
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.22132
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.22327
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.22124
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.22166
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.22324
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 1
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 1.33
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 1.33
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.95
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 1.5
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 1.33
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 1.33
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.83
09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 1.61
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.02734
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.02734
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.020804
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.029894
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.02735
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.027299
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.016612
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.029899
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2015 | 0.15183
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2020 | 0.15183
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2020 | 0.14734
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2020 | 0.154
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2030 | 0.15253
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2050 | 0.14908
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2050 | 0.14386
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2050 | 0.15381
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 1.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 1.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2015 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2030 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.13932
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.13932
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.12
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.13987
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.13713
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.12
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.14665
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.14665
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.14
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.14723
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.14435
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.13
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.15
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 2.933
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 2.933
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 2.8461
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 2.9749
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 2.9446
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 2.887
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 2.7859
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 2.9786
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.6819
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.6819
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.57962
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.78419
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.67921
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.69277
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.51958
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.86596
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 20
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 10
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 4
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 16
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 8
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 4
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 16
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 90
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 60
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 40
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 80
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 40
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 30
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 20
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 40
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2015 | 0.9797
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2020 | 0.9797
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | lower | 2020 | 0.94925
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | upper | 2020 | 0.98985
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2030 | 0.9797
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2050 | 0.9797
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | lower | 2050 | 0.9797
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | upper | 2050 | 0.98985
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 4.0232
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 3.9236
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 3.4197
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 4.6267
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 3.7171
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 3.7039
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 2.8435
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 5.0134
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 2.4548
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 2.3941
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 2.0866
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 2.8231
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 2.268
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 2.0927
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 1.735
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 2.8917
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015 | 285000
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020 | 281000
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020 | 241000
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020 | 326000
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030 | 273000
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050 | 270000
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050 | 205000
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050 | 347000
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2015 | 6.4781
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2020 | 6.3177
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | lower | 2020 | 5.5064
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | upper | 2020 | 7.4498
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2030 | 5.9851
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2050 | 5.7965
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | lower | 2050 | 4.5785
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | upper | 2050 | 7.905
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 9.2612
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 9.2612
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 6.445
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 10.4137
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 9.2246
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 9.4088
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 5.7774
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 11.35
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 0.5
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2015 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2020 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | lower | 2020 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | upper | 2020 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2030 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2050 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | lower | 2050 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | upper | 2050 | 0.2
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2015 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2020 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2020 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2020 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2030 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2050 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2050 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2050 | 0.25
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.59
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.5754
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.5015
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.6785
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.54727
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.53465
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.41045
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.72367
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.36
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.35109
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.306
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.414
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.33392
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.30207
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.25044
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.41741
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.019432
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.019432
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.01
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.26
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.01943
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.01944
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.01
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.28
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 41800
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 41200
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 35300
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 47800
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 40200
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 39000
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 29600
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 50100
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.02
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.019505
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.017
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.023
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.018551
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.016782
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.013914
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.023189
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.97318
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.97318
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.73
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.98
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.9726
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.97546
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.7
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.98
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.96585
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.96585
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.71
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.98
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.96524
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.96825
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.69
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.98
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 0.95
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 0.92649
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.8075
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 1.0925
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 0.88119
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.83672
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.66089
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 1.1411
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.2462
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.2462
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.24842
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.2462
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.2462
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.24842
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 0
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 1.36
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 1.36
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.95
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 1.53
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 1.36
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 1.36
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.83
09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 1.64
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.032838
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.032669
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.024078
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.036904
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.032701
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.032701
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.019262
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.036921
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2015 | 0.51328
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2020 | 0.51349
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2020 | 0.50249
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2020 | 0.6669
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2030 | 0.51567
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2050 | 0.51567
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2050 | 0.50323
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2050 | 0.66863
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 4.5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 5.5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 4
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 5.5
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2015 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2030 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.31768
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.31837
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.29
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.42
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.31925
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.31925
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.29
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.42
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.3344
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.33512
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.32
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.44
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.33605
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.33605
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.32
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.44
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 267.517
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 268.0993
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 262.3523
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 348.1933
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 268.8387
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 268.8387
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 262.3523
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 348.581
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.056071
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.055949
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.047557
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.064342
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.055796
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.055796
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.041847
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.069744
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 1.2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2015 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2020 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | lower | 2020 | 10
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | upper | 2020 | 30
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2030 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2050 | 10
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | lower | 2050 | 10
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | upper | 2050 | 20
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0.3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0.3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0.1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0.3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0.3
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0.1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2015 | 0.9825
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2020 | 0.9825
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | lower | 2020 | 0.95625
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | upper | 2020 | 0.99125
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2030 | 0.9825
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2050 | 0.9825
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | lower | 2050 | 0.9825
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | upper | 2050 | 0.99125
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.2891
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 1.2559
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.0412
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.4708
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 1.194
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 1.0854
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 0.86007
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.4784
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.0198
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 0.99244
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 0.86498
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.1703
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 0.94132
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 0.85153
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 0.70599
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.1767
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015 | 64000
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020 | 62000
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020 | 53000
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020 | 72000
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030 | 59000
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050 | 54000
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050 | 42000
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050 | 71000
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 2.309
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 2.2483
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 1.9062
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 2.6411
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 2.1353
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 1.937
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 1.5661
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 2.655
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 1.7169
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 1.7189
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 1.3763
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 1.9612
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 1.714
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 1.714
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 1.211
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 2.1172
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2015 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2020 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | lower | 2020 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | upper | 2020 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2030 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2050 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | lower | 2050 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | upper | 2050 | 12
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2015 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2020 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | lower | 2020 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | upper | 2020 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2030 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2050 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | lower | 2050 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | upper | 2050 | 0.15
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 0.02
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.04
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2015 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2020 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2020 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2020 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2030 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2050 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2050 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2050 | 2
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.43108
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.42088
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.34894
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.4929
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.40123
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.36476
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.28903
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.4968
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.34103
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.33259
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.28988
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.39219
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.31633
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.28616
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.23725
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.39541
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.0173
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.01664
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.01
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.13
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.016639
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.016639
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.01
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.13
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 21400
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 20900
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 17600
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 24300
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 20000
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 18300
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 14100
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 23900
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.0025
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.0024381
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.002125
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.002875
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.0023189
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.0020977
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.0017392
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.0028987
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.6682
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.66939
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.46
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.69
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.66847
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.66847
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.46
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.69
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.65148
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.65264
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.43
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.67
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.65167
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.65167
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.43
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.67
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 0.77211
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 0.75347
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.63882
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 0.88509
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 0.71756
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.65091
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.52627
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 0.89221
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.056599
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.056599
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.058575
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.056599
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.056599
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.058575
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 1
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 0.57
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 0.58
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.46
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 0.66
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 0.58
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 0.58
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.41
09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 0.71
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.032976
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.032803
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.024257
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.037051
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.032834
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.032834
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.019405
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.037069
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015 | 0.48976
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020 | 0.48902
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020 | 0.47874
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020 | 0.64336
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030 | 0.49111
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050 | 0.49111
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050 | 0.47944
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050 | 0.64501
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 4.5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 5.5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 4
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 5.5
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2015 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | lower | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | upper | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2030 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | lower | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.30038
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.30095
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.27
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.4
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.3018
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.3018
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.27
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.4
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.31619
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.31679
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.31
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.42
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.31769
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.31769
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.31
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.42
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 252.9486
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 253.4357
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 248.1088
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 333.423
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 254.1496
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 254.1496
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 248.1088
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 333.795
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.059301
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.059187
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.050309
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.068065
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.05902
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.05902
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.044265
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.073775
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 1.2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2015 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2020 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | lower | 2020 | 10
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | upper | 2020 | 30
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2030 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2050 | 10
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | lower | 2050 | 10
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | upper | 2050 | 20
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0.3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0.3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0.1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0.3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0.3
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0.1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2015 | 0.9825
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2020 | 0.9825
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | lower | 2020 | 0.95625
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | upper | 2020 | 0.99125
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2030 | 0.9825
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2050 | 0.9825
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | lower | 2050 | 0.9825
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | upper | 2050 | 0.99125
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.3634
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 1.3285
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.1015
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.5559
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 1.263
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 1.1482
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 0.90978
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.5638
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.0786
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 1.0499
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 0.91503
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.238
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 0.99573
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 0.90075
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 0.7468
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.2447
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015 | 68000
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020 | 66000
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020 | 56000
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020 | 77000
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030 | 63000
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050 | 58000
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050 | 45000
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050 | 75000
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 2.4419
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 2.3784
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 2.0165
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 2.7939
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 2.2587
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 2.0489
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 1.6566
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 2.8085
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 1.7198
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 1.7262
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 1.4559
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 1.9826
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 1.7212
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 1.7212
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 1.281
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 2.1477
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2015 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2020 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | lower | 2020 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | upper | 2020 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2030 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2050 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | lower | 2050 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | upper | 2050 | 12
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2015 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2020 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | lower | 2020 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | upper | 2020 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2030 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2050 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | lower | 2050 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | upper | 2050 | 0.15
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 0.02
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.04
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2015 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2020 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2020 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2020 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2030 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2050 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2050 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2050 | 2
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.43108
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.42088
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.34894
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.4929
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.40123
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.36476
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.28903
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.4968
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.34103
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.33259
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.28988
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.39219
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.31633
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.28616
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.23725
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.39541
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.041302
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.039725
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.13
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.039721
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.039721
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.03
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.13
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 21400
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 20900
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 17600
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 24300
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 20000
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 18300
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 14100
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 23900
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.0025
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.0024381
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.002125
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.002875
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.0023189
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.0020977
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.0017392
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.0028987
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.6614
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.66365
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.47
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.69
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.66276
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.66276
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.47
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.69
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.64559
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.64781
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.43
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.67
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.64688
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.64688
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.43
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.67
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 0.77211
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 0.75347
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.63882
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 0.88509
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 0.71756
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.65091
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.52627
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 0.89221
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.026248
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.026248
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.029392
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.026248
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.026248
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.029392
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 1
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 0.54
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 0.55
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.46
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 0.63
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 0.55
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 0.55
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.41
09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 0.68
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.025131
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.025131
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.019147
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.029424
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.025143
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.025081
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.015273
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.03051
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2015 | 0.45568
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2020 | 0.45568
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2020 | 0.44023
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2020 | 0.61598
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2030 | 0.45766
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2050 | 0.4483
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2050 | 0.43676
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2050 | 0.62512
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 2.5
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 2.5
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 2
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 2.5
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 2.5
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 1.5
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2015 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2030 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | ctrl | 2015 | 0.29303
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | ctrl | 2020 | 0.29303
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | lower | 2020 | 0.26
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | upper | 2020 | 0.4
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | ctrl | 2030 | 0.29389
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | ctrl | 2050 | 0.2898
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | lower | 2050 | 0.26
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H, F] | 1 | upper | 2050 | 0.41
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2015 | 0.30845
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2020 | 0.30845
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | lower | 2020 | 0.29
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | upper | 2020 | 0.42
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2030 | 0.30936
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2050 | 0.30505
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | lower | 2050 | 0.29
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H, F] | 1 | upper | 2050 | 0.43
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 24.6764
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 24.6764
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 23.8401
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 33.3574
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 24.749
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 24.4042
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 23.7759
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 34.0297
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.18236
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.18236
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.15501
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.20971
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.18183
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.18439
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.1383
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.23049
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 80
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 50
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 40
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 50
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 40
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 20
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 40
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 2
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2015 | 0.9825
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2020 | 0.9825
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | lower | 2020 | 0.95625
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | upper | 2020 | 0.99125
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2030 | 0.9825
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2050 | 0.9825
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | lower | 2050 | 0.9825
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | upper | 2050 | 0.99125
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.9695
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 1.9207
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.557
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 2.2649
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 1.8215
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 1.7694
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 1.2885
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 2.4074
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.1136
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 1.0861
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 0.94657
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.2807
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 1.0299
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 0.94485
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 0.78336
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.3056
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015 | 128000
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020 | 124000
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020 | 104000
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020 | 144000
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030 | 117000
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050 | 108000
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050 | 81000
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050 | 140000
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 3.0831
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.0068
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 2.5035
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 3.5456
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 2.8514
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 2.7142
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 2.0719
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 3.713
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 1.8606
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 1.8606
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 1.4953
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 2.1301
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 1.8549
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 1.8822
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 1.3341
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 2.3316
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 8
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.15
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2015 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2020 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | lower | 2020 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | upper | 2020 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2030 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2050 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | lower | 2050 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | upper | 2050 | 0.25
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.6075
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.59246
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.48025
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.69863
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.5635
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.53975
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.39306
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.73437
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.3435
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.335
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.29197
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.39503
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.31862
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.28823
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.23896
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.39827
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.01729
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.01729
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.01
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.11
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.017288
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.017298
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.01
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.13
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 39500
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 38300
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 32100
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 44400
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 36200
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 33100
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 24600
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 42700
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.003
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.0029257
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.00255
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.00345
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.0027827
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.0025173
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.002087
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.0034784
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.69234
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.69234
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.47
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.73
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.69144
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.69571
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.45
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.73
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2015 | 0.67691
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2020 | 0.67691
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, H, F] | 1 | lower | 2020 | 0.44
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, H, F] | 1 | upper | 2020 | 0.71
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2030 | 0.67597
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, H, F] | 1 | ctrl | 2050 | 0.68046
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, H, F] | 1 | lower | 2050 | 0.42
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, H, F] | 1 | upper | 2050 | 0.71
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 0.951
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 0.92746
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.77223
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 1.0937
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 0.88212
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.82797
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.63202
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 1.1326
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.056599
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.056599
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.058575
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.056599
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.056599
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.058575
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 1
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 0.57
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 0.57
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.46
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 0.66
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 0.57
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 0.57
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.41
09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 0.71
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.022902
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.022902
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.01744
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.025032
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.022911
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.02287
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.013926
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.025037
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2015 | 0.1847
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2020 | 0.1847
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2020 | 0.17996
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2020 | 0.18684
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2030 | 0.18536
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2050 | 0.18209
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2050 | 0.17664
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2050 | 0.18663
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 1.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 1.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2015 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2030 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.1464
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.1464
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.13
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.15
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.14683
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.14466
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.13
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.15
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.1541
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.1541
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.15
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.16
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.15456
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.15227
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.14
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.16
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 3.082
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 3.082
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 3.0029
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 3.1177
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 3.0912
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 3.0454
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 2.9543
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 3.1214
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.48669
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.48669
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.41369
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.5597
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.48525
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.49254
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.36941
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.61568
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | ctrl | 2015 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | ctrl | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | upper | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | ctrl | 2030 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | ctrl | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | upper | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | ctrl | 2015 | 1.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | ctrl | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | lower | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | upper | 2020 | 3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | ctrl | 2030 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | ctrl | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | upper | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | ctrl | 2015 | 90
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | ctrl | 2020 | 50
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | lower | 2020 | 40
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | upper | 2020 | 70
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | ctrl | 2030 | 40
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | ctrl | 2050 | 30
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | lower | 2050 | 20
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | upper | 2050 | 40
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | ctrl | 2015 | 2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | ctrl | 2020 | 0.3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | lower | 2020 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | upper | 2020 | 2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | ctrl | 2030 | 0.3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | ctrl | 2050 | 0.3
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | lower | 2050 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | upper | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | ctrl | 2015 | 0.9825
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | ctrl | 2020 | 0.9825
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | lower | 2020 | 0.95625
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | upper | 2020 | 0.99125
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | ctrl | 2030 | 0.9825
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | ctrl | 2050 | 0.9825
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | lower | 2050 | 0.9825
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | upper | 2050 | 0.99125
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 4.0558
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 3.9554
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 3.4474
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 4.6642
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 3.7508
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 3.704
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 2.8554
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 5.019
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 2.1609
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 2.1074
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.8368
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 2.4851
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 1.9984
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 1.835
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 1.5214
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 2.5356
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015 | 275000
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020 | 271000
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020 | 232000
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020 | 314000
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030 | 261000
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050 | 253000
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050 | 192000
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050 | 325000
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2015 | 6.2167
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2020 | 6.0628
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | lower | 2020 | 5.2842
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | upper | 2020 | 7.1492
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2030 | 5.7493
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2050 | 5.539
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | lower | 2050 | 4.3768
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | upper | 2050 | 7.5546
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 3.8885
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 3.8885
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 2.993
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 4.4295
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 3.8769
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 3.9352
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 2.6726
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 4.839
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 0.5
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2015 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2020 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | lower | 2020 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | upper | 2020 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2030 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2050 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | lower | 2050 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | upper | 2050 | 0.2
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2015 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2020 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2020 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2020 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2030 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2050 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2050 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2050 | 0.25
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.625
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.60953
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.53125
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.71875
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.57973
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.56402
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.4348
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.76425
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.333
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.32476
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.28305
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.38295
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.30888
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.27942
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.23166
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.3861
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.01729
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.01729
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.01
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.11
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.017288
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.017298
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.01
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.13
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 42500
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 41700
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 35700
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 48400
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 40300
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 38500
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 29200
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 49500
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.004
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.003901
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.0034
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.0046
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.0037103
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.0033564
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.0027827
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.0046378
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.84204
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.84204
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.74
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.86
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.84158
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.84385
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.72
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.86
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.83433
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.83433
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.72
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.85
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.83385
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.83624
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.71
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.85
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | ctrl | 2015 | 0.958
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | ctrl | 2020 | 0.93429
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | lower | 2020 | 0.8143
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | upper | 2020 | 1.1017
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | ctrl | 2030 | 0.88861
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | ctrl | 2050 | 0.84343
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | lower | 2050 | 0.66646
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | upper | 2050 | 1.1503
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.056599
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.056599
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.058575
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.056599
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.056599
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.058575
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 0
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 0.6
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 0.6
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.46
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 0.68
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 0.6
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 0.6
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.41
09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 0.74
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.028381
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.028381
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.020912
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.031371
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.028399
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.028399
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.017287
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.032976
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2015 | 0.45437
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2020 | 0.45437
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2020 | 0.43128
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2020 | 0.59666
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2030 | 0.45643
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2050 | 0.45643
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2050 | 0.44437
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2050 | 0.61083
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 2.5
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 3.5
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 3.5
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2015 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2030 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.29936
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.29936
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.26
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.30028
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.30028
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.27
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.41
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.31511
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.31511
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.29
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.42
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.31608
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.31608
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.43
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 41.595
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 41.595
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 39.481
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 54.6206
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 41.7232
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 41.7232
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 40.6204
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 55.8372
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.24041
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.24041
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.20435
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.27648
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.23967
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.23967
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.17976
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.29959
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 40
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 30
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 20
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 40
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 30
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 20
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 30
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2015 | 0.9545
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2020 | 0.9636
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | lower | 2020 | 0.909
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | upper | 2020 | 0.99818
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2030 | 0.9909
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2050 | 0.99818
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | lower | 2050 | 0.9545
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | upper | 2050 | 0.99909
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2015 | 2.139
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2020 | 2.0882
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | lower | 2020 | 1.7299
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | upper | 2020 | 2.447
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2030 | 1.9842
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2050 | 1.8031
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | lower | 2050 | 1.4271
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | upper | 2050 | 2.4588
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2015 | 1.3259
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2020 | 1.2931
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | lower | 2020 | 1.127
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | upper | 2020 | 1.5248
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2030 | 1.2261
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2050 | 1.1091
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | lower | 2050 | 0.91955
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | upper | 2050 | 1.5326
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2015 | 126000
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2020 | 122000
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | lower | 2020 | 103000
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | upper | 2020 | 142000
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2030 | 115000
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2050 | 103000
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | lower | 2050 | 79000
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | upper | 2050 | 133000
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 3.4649
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.3813
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 2.8569
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 3.9717
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 3.2103
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 2.9122
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 2.3466
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 3.9914
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 2.1064
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 2.1064
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 1.6178
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 2.3975
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 2.0998
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 2.0998
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 1.4231
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 2.5798
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 8
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.4
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 0.02
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.04
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2015 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2020 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | lower | 2020 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | upper | 2020 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2030 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2050 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | lower | 2050 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | upper | 2050 | 2
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.67403
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.65802
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.54513
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.77107
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.62718
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.56994
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.45108
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.77719
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.4178
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.40746
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.35513
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.48047
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.38754
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.35057
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.29066
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.48443
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.017679
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.017679
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.01
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.15
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.017677
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.017677
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.01
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.15
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2015 | 39700
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2020 | 38500
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | lower | 2020 | 32500
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | upper | 2020 | 44600
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2030 | 36300
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2050 | 32400
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | lower | 2050 | 24900
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | upper | 2050 | 41900
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.065
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.063391
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.05525
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.07475
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.060292
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.054541
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.045219
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.075365
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.70927
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.70927
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.48
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.74
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.70831
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.70831
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.47
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.73
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.69351
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.69351
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.45
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.72
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.69251
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.69251
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.44
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.71
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 1.0918
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 1.0655
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.90026
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 1.2515
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 1.0147
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.92052
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.74174
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 1.2616
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.088886
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.088886
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.090904
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.088886
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.088886
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.090904
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 1
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 0.66
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 0.66
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.51
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 0.76
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 0.66
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 0.66
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.45
09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 0.82
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.028554
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.028554
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.021147
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.031556
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.028572
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.028572
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.017474
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.03316
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015 | 0.42889
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020 | 0.42889
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020 | 0.40569
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020 | 0.57212
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030 | 0.43085
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050 | 0.43085
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050 | 0.41935
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050 | 0.5869
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 2.5
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 3.5
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 3.5
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2015 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | lower | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | upper | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2030 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | lower | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.28061
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.28061
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.38
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.2815
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.2815
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.39
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.29538
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.29538
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.27
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.29632
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.29632
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.28
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.41
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 38.9906
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 38.9906
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 36.8812
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 52.0111
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 39.1138
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 39.1138
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 38.0699
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 53.2806
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.25647
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.25647
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.218
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.29494
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.25566
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.25566
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.19175
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.31958
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 40
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 30
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 20
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 40
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 30
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 20
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 30
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0.3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2015 | 0.9545
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2020 | 0.9636
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | lower | 2020 | 0.909
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | upper | 2020 | 0.99818
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2030 | 0.9909
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2050 | 0.99818
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | lower | 2050 | 0.9545
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | upper | 2050 | 0.99909
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2015 | 2.2819
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2020 | 2.2277
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | lower | 2020 | 1.8455
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | upper | 2020 | 2.6104
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2030 | 2.1166
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2050 | 1.9234
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | lower | 2050 | 1.5223
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] |  | upper | 2050 | 2.6228
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2015 | 1.4144
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2020 | 1.3794
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | lower | 2020 | 1.2023
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | upper | 2020 | 1.6266
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2030 | 1.3079
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | ctrl | 2050 | 1.1831
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | lower | 2050 | 0.9809
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] |  | upper | 2050 | 1.6348
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2015 | 134000
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2020 | 130000
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | lower | 2020 | 110000
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | upper | 2020 | 151000
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2030 | 123000
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2050 | 109000
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | lower | 2050 | 84000
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | upper | 2050 | 142000
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 3.6963
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.6071
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 3.0478
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 4.237
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 3.4244
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 3.1065
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 2.5032
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 4.2577
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 2.1422
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 2.1422
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 1.7259
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 2.4568
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 2.1352
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 2.1352
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 1.518
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 2.6514
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 8
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.4
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 0.02
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2015 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2020 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | lower | 2020 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | upper | 2020 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2030 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2050 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | lower | 2050 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | upper | 2050 | 2
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.67403
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.65802
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.54513
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.77107
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.62718
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.56994
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.45108
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.77719
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.4178
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.40746
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.35513
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.48047
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.38754
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.35057
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.29066
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.48443
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.042201
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.042201
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.15
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.042197
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.042197
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.04
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.15
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2015 | 39700
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2020 | 38500
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | lower | 2020 | 32500
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | upper | 2020 | 44600
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2030 | 36300
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2050 | 32400
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | lower | 2050 | 24900
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | upper | 2050 | 41900
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.065
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.063391
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.05525
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.07475
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.060292
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.054541
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.045219
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.075365
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.70348
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.70348
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.49
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.73
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.70257
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.70257
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.49
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.72
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.68871
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.68871
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.47
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.71
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.68775
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.68775
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.46
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.7
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 1.0918
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 1.0655
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.90026
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 1.2515
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 1.0147
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.92052
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.74174
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 1.2616
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.057896
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.057896
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.061106
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.057896
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.057896
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.061106
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 1
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 0.63
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 0.63
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.51
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 0.73
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 0.63
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 0.63
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.45
09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 0.79
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.02847
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.02847
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.02091
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.031682
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.028488
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.028396
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.017285
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.032112
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2015 | 0.46058
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2020 | 0.46058
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2020 | 0.4312
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2020 | 0.46845
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2030 | 0.46271
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2050 | 0.45267
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2050 | 0.44062
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2050 | 0.46798
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 2.5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 2.5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 2.5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 2.5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 1.5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2015 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2030 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.30027
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.30027
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.26
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.31
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.3012
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.29677
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.27
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.31
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.31607
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.31607
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.29
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.33
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.31706
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.31239
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.33
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 25.2858
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 25.2858
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 23.6731
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 25.718
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 25.3645
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 24.9912
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 24.3259
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 25.8365
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 3.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 4.6
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 5
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.27684
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.27684
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.23531
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.31836
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.27598
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.2801
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.21007
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.35012
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 1.2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 90
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 70
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 20
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 90
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 50
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 30
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 10
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 50
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2015 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2020 | 0.3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | lower | 2020 | 0.1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | upper | 2020 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2030 | 0.3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | ctrl | 2050 | 0.3
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | lower | 2050 | 0.1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2] | upper | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2015 | 0.9545
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2020 | 0.9636
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | lower | 2020 | 0.909
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | upper | 2020 | 0.99818
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2030 | 0.9909
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | ctrl | 2050 | 0.99818
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | lower | 2050 | 0.9545
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2] | upper | 2050 | 0.99909
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 2.2167
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 2.1618
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 1.7699
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 2.6441
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 2.0497
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 1.9779
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 1.5616
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 2.6965
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 1.4459
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 1.4101
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 1.229
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 1.6628
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 1.337
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 1.2275
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 1.0177
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 1.6962
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | 1 | ctrl | 2015 | 147000
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | 1 | ctrl | 2020 | 143000
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | 1 | lower | 2020 | 120000
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | 1 | upper | 2020 | 168000
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | 1 | ctrl | 2030 | 134000
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | 1 | ctrl | 2050 | 124000
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | 1 | lower | 2050 | 95000
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J | 1 | upper | 2050 | 160000
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 3.6625
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.5719
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 2.9989
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 4.3068
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 3.3867
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 3.2054
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 2.5794
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 4.3926
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L | 1 | ctrl | 2015 | 2.099
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L | 1 | ctrl | 2020 | 2.099
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L | 1 | lower | 2020 | 1.6129
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L | 1 | upper | 2020 | 2.3893
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L | 1 | ctrl | 2030 | 2.0923
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L | 1 | ctrl | 2050 | 2.1247
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L | 1 | lower | 2050 | 1.4399
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L | 1 | upper | 2050 | 2.6104
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 8
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.4
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.04
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2015 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2020 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | lower | 2020 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | upper | 2020 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2030 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | ctrl | 2050 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | lower | 2050 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E | 1 | upper | 2050 | 2
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.457
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.44569
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.38845
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.52555
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.4239
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.38346
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.31792
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.52987
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.017669
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.017669
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.01
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.15
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.017667
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.017677
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.01
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.15
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2015 | 46600
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2020 | 45200
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | lower | 2020 | 38000
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | upper | 2020 | 53000
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2030 | 42600
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2050 | 38700
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | lower | 2050 | 29600
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | upper | 2050 | 49900
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.07
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.068267
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.0595
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.0805
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.06493
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.058736
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.048697
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.081162
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.70205
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.70205
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.56
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.74
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.70107
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.70573
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.56
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.73
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.68625
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.68625
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.53
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.72
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.68522
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.69011
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.53
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.71
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 1.1576
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 1.129
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.94786
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 1.3613
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 1.0738
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 1.0013
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.80577
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 1.3722
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.088886
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.088886
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.090904
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.088886
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.088886
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.090904
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 0
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 0.66
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 0.66
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.51
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 0.76
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 0.66
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 0.66
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.45
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 0.82
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.70063
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.68328
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.55941
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.83572
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.64988
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.61789
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.48784
09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.84235
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2015 | 0.023732
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2020 | 0.023732
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2020 | 0.018068
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2020 | 0.025941
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2030 | 0.023741
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | ctrl | 2050 | 0.023698
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | lower | 2050 | 0.014428
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  |  | 1 | upper | 2050 | 0.025902
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2015 | 0.17819
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2020 | 0.17819
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2020 | 0.17348
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2020 | 0.18034
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2030 | 0.17885
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | ctrl | 2050 | 0.17553
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | lower | 2050 | 0.17012
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cb coefficient (40°C/80°C) | Cb coefficient | 40°C/80°C |  |  |  |  | upper | 2050 | 0.17742
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 1.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 1.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2015 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2030 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | lower | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Cv coefficient (40°C/80°C) | Cv coefficient | 40°C/80°C |  |  | I |  | upper | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.14486
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.14486
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.13
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.15
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.14532
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.14304
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.13
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.15
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.15249
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.15249
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.14
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.16
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.15297
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.15057
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.14
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.16
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.04
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 3.0497
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 3.0497
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 2.9692
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 3.0866
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 3.0594
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 3.0113
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 2.9184
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 3.0437
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 3.4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 4.6
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 3
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.9837
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.9837
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.83615
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 1.1313
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.9806
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.99623
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.74718
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 1.2453
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | ctrl | 2015 | 16
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | ctrl | 2020 | 11
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | lower | 2020 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | upper | 2020 | 16
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | ctrl | 2030 | 8
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | ctrl | 2050 | 4
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | lower | 2050 | 2
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 1 | upper | 2050 | 16
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | ctrl | 2015 | 1.2
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | ctrl | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | lower | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | upper | 2020 | 3
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | ctrl | 2030 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | lower | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | 1 | upper | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | ctrl | 2015 | 90
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | ctrl | 2020 | 70
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | lower | 2020 | 50
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | upper | 2020 | 90
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | ctrl | 2030 | 50
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | ctrl | 2050 | 40
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | lower | 2050 | 40
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | 1 | upper | 2050 | 50
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | ctrl | 2015 | 2
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | ctrl | 2020 | 0.3
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | lower | 2020 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | upper | 2020 | 2
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | ctrl | 2030 | 0.3
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | ctrl | 2050 | 0.3
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | lower | 2050 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | 1 | upper | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | ctrl | 2015 | 0.9545
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | ctrl | 2020 | 0.9636
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | lower | 2020 | 0.909
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | upper | 2020 | 0.99818
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | ctrl | 2030 | 0.9909
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | ctrl | 2050 | 0.99818
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | lower | 2050 | 0.9545
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | 1 | upper | 2050 | 0.99909
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 3.8692
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 3.7735
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 3.2888
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 4.4496
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 3.5777
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 3.5509
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 2.9889
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 4.8063
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 2.9839
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 2.91
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 2.5363
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 3.4315
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 2.759
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 2.5356
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 2.1023
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 3.5038
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2015 | 318000
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2020 | 313000
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | lower | 2020 | 268000
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | upper | 2020 | 362000
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2030 | 302000
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | ctrl | 2050 | 293000
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | lower | 2050 | 227000
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | J |  | upper | 2050 | 375000
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2015 | 6.8531
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2020 | 6.6835
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | lower | 2020 | 5.8251
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | upper | 2020 | 7.8811
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2030 | 6.3367
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2050 | 6.0865
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | lower | 2050 | 5.0912
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | upper | 2050 | 8.3101
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 4.5161
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 4.5161
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 3.3432
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 5.1194
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 4.5019
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 4.5737
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 2.9875
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 5.5829
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2015 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | lower | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | upper | 2020 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2030 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | ctrl | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | lower | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | D | 1 | upper | 2050 | 0.5
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2015 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2020 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2020 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2020 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2030 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2050 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2050 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2050 | 0.25
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.455
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.44374
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.38675
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.52325
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.42204
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.38179
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.31653
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.52755
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.017669
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.017669
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.01
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.14
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.017667
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.017677
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.01
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.15
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2015 | 48600
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2020 | 47700
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | lower | 2020 | 40800
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | upper | 2020 | 55300
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2030 | 46100
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | ctrl | 2050 | 44100
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | lower | 2050 | 34200
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 | J |  | upper | 2050 | 56500
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2015 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2020 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2030 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | ctrl | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | lower | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [C, M] |  | upper | 2050 | 1
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.08
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.07802
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.068
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.092
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.074206
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.067127
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.055654
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.092757
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2015 | 0.86339
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2020 | 0.86339
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2020 | 0.73
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2020 | 0.88
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2030 | 0.86291
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | ctrl | 2050 | 0.86529
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | lower | 2050 | 0.72
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, H] | 1 | upper | 2050 | 0.88
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2015 | 0.85577
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2020 | 0.85577
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2020 | 0.72
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2020 | 0.87
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2030 | 0.85526
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | ctrl | 2050 | 0.85776
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | lower | 2050 | 0.71
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, H] | 1 | upper | 2050 | 0.87
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | ctrl | 2015 | 1.045
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | ctrl | 2020 | 1.0191
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | lower | 2020 | 0.88825
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | upper | 2020 | 1.2018
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | ctrl | 2030 | 0.96931
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | ctrl | 2050 | 0.91643
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | lower | 2050 | 0.76657
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [E, J, K] | 1 | upper | 2050 | 1.2512
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2015 | 0.088886
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2020 | 0.088886
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2020 | 0.090904
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2030 | 0.088886
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | ctrl | 2050 | 0.088886
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | lower | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [C, L] |  | upper | 2050 | 0.090904
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 0
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 0.69
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 0.69
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.51
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 0.78
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 0.69
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 0.69
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.45
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 0.84
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.59
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.5754
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.5015
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.6785
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.54727
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.53465
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.45003
09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.72367
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2015 | 0.022162
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2020 | 0.022162
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | lower | 2020 | 0.021135
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | upper | 2020 | 0.024723
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2030 | 0.022162
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2050 | 0.022162
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | lower | 2050 | 0.01691
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | upper | 2050 | 0.024702
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 1.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 1.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2015 | 6.8407
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2020 | 6.8407
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | lower | 2020 | 5.3402
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | upper | 2020 | 6.8643
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2030 | 6.8407
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2050 | 6.8407
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | lower | 2050 | 5.3402
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | upper | 2050 | 6.8703
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 1.7
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 2.3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 1.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 2.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2015 | 0.21928
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2020 | 0.21928
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | lower | 2020 | 0.18638
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | upper | 2020 | 0.25217
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2030 | 0.21928
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2050 | 0.21928
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | lower | 2050 | 0.16446
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | upper | 2050 | 0.27409
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2015 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2020 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | upper | 2020 | 1.15
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2030 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2050 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | lower | 2050 | 0.89
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | upper | 2050 | 1.15
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2015 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2020 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | upper | 2020 | 1.15
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2030 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2050 | 1.1401
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | lower | 2050 | 0.89
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | upper | 2050 | 1.15
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | ctrl | 2015 | 16
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | ctrl | 2020 | 11
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | lower | 2020 | 4
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | upper | 2020 | 16
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | ctrl | 2030 | 8
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | ctrl | 2050 | 4
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | lower | 2050 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | upper | 2050 | 16
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | ctrl | 2015 | 4
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | ctrl | 2020 | 3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | lower | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | upper | 2020 | 4
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | ctrl | 2030 | 3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | ctrl | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | lower | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | upper | 2050 | 4
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | ctrl | 2015 | 90
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | ctrl | 2020 | 60
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | lower | 2020 | 40
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | upper | 2020 | 80
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | ctrl | 2030 | 50
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | ctrl | 2050 | 40
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | lower | 2050 | 30
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | upper | 2050 | 40
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | ctrl | 2015 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | ctrl | 2020 | 0.3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | lower | 2020 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | upper | 2020 | 2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | ctrl | 2030 | 0.3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | ctrl | 2050 | 0.3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | lower | 2050 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | upper | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2015 | 0.9797
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2020 | 0.9797
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | lower | 2020 | 0.8985
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | upper | 2020 | 0.98985
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2030 | 0.9797
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2050 | 0.9797
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | lower | 2050 | 0.9797
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | upper | 2050 | 0.98985
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.40931
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.39918
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.34792
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.47071
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.37967
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.34345
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.28475
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.47458
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.29821
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.29083
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.25348
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.34295
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.27661
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.25023
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.20746
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.34577
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2015 | 1.3962
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 1.5292
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2020 | 1.5127
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2020 | 1.9935
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 2.2384
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 2.593
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2050 | 2.563
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2050 | 3.3802
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2015 | 1.1912
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 1.1912
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | lower | 2020 | 0.82614
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | upper | 2020 | 1.7159
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 1.1912
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 1.1912
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | lower | 2050 | 0.72831
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | upper | 2050 | 1.8408
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2015 | 33000
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2020 | 32500
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2020 | 27800
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2020 | 37700
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2030 | 31500
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2050 | 29600
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2050 | 22800
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2050 | 38000
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.70753
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.69002
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.6014
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.81366
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.65628
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.59368
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.49221
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.82035
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2015 | 2.5874
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 2.7204
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | lower | 2020 | 2.3388
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | upper | 2020 | 3.7093
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 3.4296
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 3.7842
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | lower | 2050 | 3.2914
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | upper | 2050 | 5.221
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 0.5
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2015 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2020 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | lower | 2020 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | upper | 2020 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2030 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2050 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | lower | 2050 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | upper | 2050 | 0.2
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2015 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2020 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | lower | 2020 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | upper | 2020 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2030 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2050 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | lower | 2050 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | upper | 2050 | 0.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2015 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2020 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | lower | 2020 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | upper | 2020 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2030 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2050 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | lower | 2050 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | upper | 2050 | 0.25
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2015 | 0.46667
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2020 | 0.45512
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | lower | 2020 | 0.39667
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | upper | 2020 | 0.53667
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2030 | 0.43287
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2050 | 0.39157
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | lower | 2050 | 0.32465
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | upper | 2050 | 0.54108
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2015 | 0.34
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2020 | 0.33158
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | lower | 2020 | 0.289
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | upper | 2020 | 0.391
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2030 | 0.31537
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2050 | 0.28529
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | lower | 2050 | 0.23653
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | upper | 2050 | 0.39422
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2015 | 0.019432
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2020 | 0.019432
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | lower | 2020 | 0.01
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | upper | 2020 | 0.26
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2030 | 0.019432
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2050 | 0.019432
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | lower | 2050 | 0.01
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | upper | 2050 | 0.26
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 37700
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 37100
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 31700
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 42900
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 35900
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 33700
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 26000
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 43300
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2015 | 0.02
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2020 | 0.019505
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | lower | 2020 | 0.017
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | upper | 2020 | 0.023
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2030 | 0.018551
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2050 | 0.016782
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | lower | 2050 | 0.013914
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | upper | 2050 | 0.023189
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | ctrl | 2015 | 0.80667
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | ctrl | 2020 | 0.7867
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | lower | 2020 | 0.68567
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | upper | 2020 | 0.92767
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | ctrl | 2030 | 0.74824
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | ctrl | 2050 | 0.67686
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | lower | 2050 | 0.56118
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | upper | 2050 | 0.9353
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2015 | 0.2462
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2020 | 0.2462
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | lower | 2020 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | upper | 2020 | 0.24842
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2030 | 0.2462
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2050 | 0.2462
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | lower | 2050 | 0
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | upper | 2050 | 0.24842
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2015 | 2.95
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2020 | 3.1
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | lower | 2020 | 2.68
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | upper | 2020 | 3.3
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2030 | 3.91
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2050 | 4.31
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | lower | 2050 | 3.77
09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | upper | 2050 | 4.65
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2015 | 0.022039
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2020 | 0.022039
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | lower | 2020 | 0.02098
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | upper | 2020 | 0.024587
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2030 | 0.022039
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2050 | 0.022026
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | lower | 2050 | 0.017093
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | upper | 2050 | 0.024549
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 1.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 2.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 1.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 2.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2015 | 51.6377
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2020 | 51.6377
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | lower | 2020 | 40.3835
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | upper | 2020 | 51.8149
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2030 | 51.6377
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2050 | 51.637
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | lower | 2050 | 39.6586
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | upper | 2050 | 51.8599
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 1.7
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 2.3
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 1.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 2.5
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2015 | 0.058097
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2020 | 0.058097
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | lower | 2020 | 0.049383
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | upper | 2020 | 0.066812
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2030 | 0.058097
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2050 | 0.058098
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | lower | 2050 | 0.043573
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | upper | 2050 | 0.072622
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2015 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2020 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | upper | 2020 | 1.16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2030 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2050 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | lower | 2050 | 0.88
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | upper | 2050 | 1.16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2015 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2020 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | upper | 2020 | 1.16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2030 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2050 | 1.1475
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | lower | 2050 | 0.88
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | upper | 2050 | 1.16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | ctrl | 2015 | 16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | ctrl | 2020 | 11
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | lower | 2020 | 4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | upper | 2020 | 16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | ctrl | 2030 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | ctrl | 2050 | 4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | lower | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | I | 2 | upper | 2050 | 16
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | ctrl | 2015 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | ctrl | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | lower | 2020 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | upper | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | ctrl | 2030 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | ctrl | 2050 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | lower | 2050 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 2 | upper | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | ctrl | 2015 | 90
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | ctrl | 2020 | 60
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | lower | 2020 | 40
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | upper | 2020 | 80
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | ctrl | 2030 | 40
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | ctrl | 2050 | 30
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | lower | 2050 | 20
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | I | 2 | upper | 2050 | 40
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | ctrl | 2015 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | ctrl | 2020 | 0.3
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | lower | 2020 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | upper | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | ctrl | 2030 | 0.3
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | ctrl | 2050 | 0.3
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | lower | 2050 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | I | 2 | upper | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2015 | 0.9797
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2020 | 0.9797
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | lower | 2020 | 0.94925
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | upper | 2020 | 0.98985
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2030 | 0.9797
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2050 | 0.9797
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | lower | 2050 | 0.9797
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | upper | 2050 | 0.98985
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.36988
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.36073
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.3144
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.42537
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.34309
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.3397
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.25732
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.45821
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.13614
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.13277
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.11572
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.15656
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.12628
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.11424
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.094711
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.15785
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2015 | 1.3885
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 1.5207
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2020 | 1.5043
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2020 | 1.9788
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 2.226
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 2.577
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2050 | 2.5489
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2050 | 3.4145
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2015 | 1.1836
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 1.1836
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | lower | 2020 | 0.82084
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | upper | 2020 | 1.7017
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 1.1836
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 1.1836
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | lower | 2050 | 0.72364
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | upper | 2050 | 1.859
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2015 | 42800
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2020 | 42000
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2020 | 35800
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2020 | 48500
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2030 | 40500
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2050 | 38200
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2050 | 28800
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2050 | 48500
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.50603
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.4935
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.43012
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.58193
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.46937
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.45394
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.35204
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.61606
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2015 | 2.572
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 2.7043
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | lower | 2020 | 2.3252
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | upper | 2020 | 3.6806
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 3.4095
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 3.7606
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | lower | 2050 | 3.2726
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | upper | 2050 | 5.2735
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 8
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2015 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2020 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | lower | 2020 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | upper | 2020 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2030 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2050 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | lower | 2050 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | upper | 2050 | 0.4
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2015 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2020 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | lower | 2020 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | upper | 2020 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2030 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2050 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | lower | 2050 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | upper | 2050 | 0.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2015 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | lower | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | upper | 2020 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2030 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | lower | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | upper | 2050 | 2
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2015 | 0.42444
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2020 | 0.41394
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | lower | 2020 | 0.36078
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | upper | 2020 | 0.48811
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2030 | 0.3937
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2050 | 0.38981
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | lower | 2050 | 0.29528
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | upper | 2050 | 0.52579
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2015 | 0.15622
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2020 | 0.15236
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | lower | 2020 | 0.13279
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | upper | 2020 | 0.17966
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2030 | 0.14491
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2050 | 0.13108
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | lower | 2050 | 0.10868
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | upper | 2050 | 0.18113
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2015 | 0.019432
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2020 | 0.019432
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | lower | 2020 | 0.01
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | upper | 2020 | 0.26
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2030 | 0.019432
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2050 | 0.019442
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | lower | 2050 | 0.01
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | upper | 2050 | 0.28
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 49100
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 48200
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 41100
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 55600
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 46400
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 43900
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 33000
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 55700
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2015 | 0.017
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2020 | 0.016579
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | lower | 2020 | 0.01445
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | upper | 2020 | 0.01955
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2030 | 0.015769
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2050 | 0.014265
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | lower | 2050 | 0.011827
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | upper | 2050 | 0.019711
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | ctrl | 2015 | 0.58067
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | ctrl | 2020 | 0.56629
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | lower | 2020 | 0.49357
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | upper | 2020 | 0.66777
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | ctrl | 2030 | 0.53861
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | ctrl | 2050 | 0.52089
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | lower | 2050 | 0.40396
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | upper | 2050 | 0.70692
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2015 | 0.2462
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2020 | 0.2462
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | lower | 2020 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | upper | 2020 | 0.24842
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2030 | 0.2462
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2050 | 0.2462
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | lower | 2050 | 0
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | upper | 2050 | 0.24842
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2015 | 2.95
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2020 | 3.1
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | lower | 2020 | 2.68
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | upper | 2020 | 3.3
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2030 | 3.91
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2050 | 4.32
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | lower | 2050 | 3.77
09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | upper | 2050 | 4.65
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2015 | 0.022012
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2020 | 0.022012
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | lower | 2020 | 0.020946
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | upper | 2020 | 0.024556
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2030 | 0.022012
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2050 | 0.021998
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | lower | 2050 | 0.017064
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | upper | 2050 | 0.024519
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 2.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 2.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 2.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 2.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2015 | 103.4256
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2020 | 103.4256
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | lower | 2020 | 80.9174
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | upper | 2020 | 103.7801
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2030 | 103.4256
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2050 | 103.4242
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | lower | 2050 | 79.4676
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | upper | 2050 | 103.8701
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 1.7
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 2.3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 1.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 2.5
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2015 | 0.048344
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2020 | 0.048344
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | lower | 2020 | 0.041092
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | upper | 2020 | 0.055595
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2030 | 0.048344
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2050 | 0.048345
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | lower | 2050 | 0.036258
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | upper | 2050 | 0.060431
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2015 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2020 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | upper | 2020 | 1.16
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2030 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2050 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | lower | 2050 | 0.88
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | upper | 2050 | 1.16
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2015 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2020 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | lower | 2020 | 0.89
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | upper | 2020 | 1.16
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2030 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2050 | 1.1492
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | lower | 2050 | 0.88
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | upper | 2050 | 1.16
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 3 | ctrl | 2015 | 3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 3 | ctrl | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 3 | lower | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 3 | upper | 2020 | 3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 3 | ctrl | 2030 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 3 | ctrl | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 3 | lower | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | 3 | upper | 2050 | 3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 3 | ctrl | 2015 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 3 | ctrl | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 3 | lower | 2020 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 3 | upper | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 3 | ctrl | 2030 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 3 | ctrl | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 3 | lower | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | 3 | upper | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [2, 3] | ctrl | 2015 | 90
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [2, 3] | ctrl | 2020 | 60
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [2, 3] | lower | 2020 | 40
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [2, 3] | upper | 2020 | 60
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [2, 3] | ctrl | 2030 | 40
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [2, 3] | ctrl | 2050 | 20
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [2, 3] | lower | 2050 | 20
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [2, 3] | upper | 2050 | 40
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 3 | ctrl | 2015 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 3 | ctrl | 2020 | 0.3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 3 | lower | 2020 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 3 | upper | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 3 | ctrl | 2030 | 0.3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 3 | ctrl | 2050 | 0.3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 3 | lower | 2050 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | 3 | upper | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2015 | 0.9797
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2020 | 0.9797
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | lower | 2020 | 0.94925
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | upper | 2020 | 0.98985
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2030 | 0.9797
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2050 | 0.9797
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | lower | 2050 | 0.9797
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | upper | 2050 | 0.98985
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.33937
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.33097
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.28847
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.39028
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.31479
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.31027
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.2361
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.41899
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.11119
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.10844
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.094512
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.12787
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.10314
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.0933
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.077354
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.12892
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2015 | 1.3867
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 1.5188
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2020 | 1.5025
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2020 | 1.9755
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 2.2232
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 2.5738
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2050 | 2.5458
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2050 | 3.4087
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2015 | 1.1818
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 1.1818
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | lower | 2020 | 0.81965
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | upper | 2020 | 1.6986
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 1.1818
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 1.1819
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | lower | 2050 | 0.7226
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M |  | upper | 2050 | 1.8555
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2015 | 35200
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2020 | 34600
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2020 | 29500
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2020 | 39900
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2030 | 33300
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | ctrl | 2050 | 31400
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | lower | 2050 | 23600
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  |  | upper | 2050 | 39900
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.45057
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.43941
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.38298
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.51815
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.41793
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.40357
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.31345
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.54792
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2015 | 2.5686
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 2.7007
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | lower | 2020 | 2.3221
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | upper | 2020 | 3.6741
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 3.405
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 3.7556
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | lower | 2050 | 3.2684
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | M |  | upper | 2050 | 5.2642
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 8
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2015 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2020 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | lower | 2020 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | upper | 2020 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2030 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2050 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | lower | 2050 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | upper | 2050 | 0.4
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2015 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2020 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | lower | 2020 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | upper | 2020 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2030 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2050 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | lower | 2050 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | upper | 2050 | 0.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2015 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | lower | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | upper | 2020 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2030 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2050 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | lower | 2050 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | upper | 2050 | 2
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2015 | 0.39
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2020 | 0.38035
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | lower | 2020 | 0.3315
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | upper | 2020 | 0.4485
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2030 | 0.36175
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2050 | 0.35655
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | lower | 2050 | 0.27131
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | upper | 2050 | 0.48149
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2015 | 0.12778
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2020 | 0.12462
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | lower | 2020 | 0.10861
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | upper | 2020 | 0.14694
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2030 | 0.11852
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2050 | 0.10722
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | lower | 2050 | 0.088892
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | upper | 2050 | 0.14815
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2015 | 0.019432
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2020 | 0.019432
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | lower | 2020 | 0.01
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | upper | 2020 | 0.26
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2030 | 0.019432
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2050 | 0.019442
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | lower | 2050 | 0.01
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | upper | 2050 | 0.28
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 40500
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 39700
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 33900
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 45900
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 38200
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 36100
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 27200
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 45800
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2015 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | lower | 2020 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | upper | 2020 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2030 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | lower | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | upper | 2050 | 1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2015 | 0.015
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2020 | 0.014629
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | lower | 2020 | 0.01275
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | upper | 2020 | 0.01725
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2030 | 0.013914
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2050 | 0.012586
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | lower | 2050 | 0.010435
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | upper | 2050 | 0.017392
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | ctrl | 2015 | 0.51778
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | ctrl | 2020 | 0.50496
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | lower | 2020 | 0.44011
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | upper | 2020 | 0.59544
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | ctrl | 2030 | 0.48027
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | ctrl | 2050 | 0.46376
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | lower | 2050 | 0.36021
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | L | 1 | upper | 2050 | 0.62964
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2015 | 0.2462
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2020 | 0.2462
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | lower | 2020 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | upper | 2020 | 0.24842
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2030 | 0.2462
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2050 | 0.2462
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | lower | 2050 | 0
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | upper | 2050 | 0.24842
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2015 | 2.95
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2020 | 3.1
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | lower | 2020 | 2.68
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | upper | 2020 | 3.3
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2030 | 3.91
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2050 | 4.32
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | lower | 2050 | 3.77
09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | upper | 2050 | 4.65
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2015 | 0.020554
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2020 | 0.020554
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | lower | 2020 | 0.017045
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | upper | 2020 | 0.022952
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2030 | 0.020554
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | ctrl | 2050 | 0.020554
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | lower | 2050 | 0.013836
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, K] |  | upper | 2050 | 0.022915
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 1.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 1.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2015 | 6.0703
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2020 | 6.0703
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | lower | 2020 | 5.4461
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | upper | 2020 | 6.0926
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2030 | 6.0703
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2050 | 6.0703
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | lower | 2050 | 5.3681
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | upper | 2050 | 6.0986
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.55
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.45
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.75
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2015 | 0.16474
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2020 | 0.16474
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | lower | 2020 | 0.14003
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | upper | 2020 | 0.18945
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2030 | 0.16474
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2050 | 0.16474
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | lower | 2050 | 0.12355
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | upper | 2050 | 0.20592
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2015 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2020 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | lower | 2020 | 0.9
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | upper | 2020 | 1.02
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2030 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2050 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | lower | 2050 | 0.89
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | upper | 2050 | 1.02
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2015 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2020 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | lower | 2020 | 0.9
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | upper | 2020 | 1.02
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2030 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2050 | 1.0117
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | lower | 2050 | 0.89
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | upper | 2050 | 1.02
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | ctrl | 2015 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | ctrl | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | lower | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | upper | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | ctrl | 2030 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | ctrl | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | upper | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | ctrl | 2015 | 1.2
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | ctrl | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | lower | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | upper | 2020 | 3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | ctrl | 2030 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | ctrl | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | upper | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | ctrl | 2015 | 90
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | ctrl | 2020 | 50
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | lower | 2020 | 40
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | upper | 2020 | 70
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | ctrl | 2030 | 40
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | ctrl | 2050 | 40
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | lower | 2050 | 20
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | upper | 2050 | 40
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | ctrl | 2015 | 2
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | ctrl | 2020 | 0.3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | lower | 2020 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | upper | 2020 | 2
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | ctrl | 2030 | 0.3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | ctrl | 2050 | 0.3
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | lower | 2050 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | upper | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2015 | 0.9825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2020 | 0.9825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | lower | 2020 | 0.9125
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | upper | 2020 | 0.99125
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2030 | 0.9825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2050 | 0.9825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | lower | 2050 | 0.9825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | upper | 2050 | 0.99125
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.44479
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.43378
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.37807
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.51151
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.41257
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.37322
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.30943
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.5655
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.28796
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.28083
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.24477
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.33116
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.2671
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.24162
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.20033
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.33388
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2015 | 1.2949
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2020 | 1.4182
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, M] |  | lower | 2020 | 1.4017
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, M] |  | upper | 2020 | 1.6106
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2030 | 2.0759
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2050 | 2.4048
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, M] |  | lower | 2050 | 2.3749
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, M] |  | upper | 2050 | 2.769
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2015 | 0.54352
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2020 | 0.54352
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, M] |  | lower | 2020 | 0.41292
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, M] |  | upper | 2020 | 0.68951
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2030 | 0.54352
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2050 | 0.54352
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, M] |  | lower | 2050 | 0.36398
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, M] |  | upper | 2050 | 0.75467
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2015 | 33600
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2020 | 32700
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | lower | 2020 | 28000
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | upper | 2020 | 37900
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2030 | 31000
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2050 | 27900
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | lower | 2050 | 21700
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | upper | 2050 | 37100
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2015 | 0.73275
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.71462
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | lower | 2020 | 0.62284
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | upper | 2020 | 0.84266
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2030 | 0.67968
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2050 | 0.61484
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | lower | 2050 | 0.50976
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | upper | 2050 | 0.89938
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2015 | 1.8384
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2020 | 1.9617
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, M] |  | lower | 2020 | 1.8147
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, M] |  | upper | 2020 | 2.3001
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2030 | 2.6195
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, M] |  | ctrl | 2050 | 2.9483
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, M] |  | lower | 2050 | 2.7389
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, M] |  | upper | 2050 | 3.5237
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 0.5
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2015 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2020 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | lower | 2020 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | upper | 2020 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2030 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2050 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | lower | 2050 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | upper | 2050 | 0.4
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2015 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2020 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | lower | 2020 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | upper | 2020 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2030 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2050 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | lower | 2050 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | upper | 2050 | 0.1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2015 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2020 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | lower | 2020 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | upper | 2020 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2030 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2050 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | lower | 2050 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | upper | 2050 | 0.25
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2015 | 0.45
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2020 | 0.43886
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | lower | 2020 | 0.3825
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | upper | 2020 | 0.5175
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2030 | 0.41741
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | ctrl | 2050 | 0.37759
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | lower | 2050 | 0.31305
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | L |  | upper | 2050 | 0.57212
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2015 | 0.29133
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2020 | 0.28412
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | lower | 2020 | 0.24763
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | upper | 2020 | 0.33503
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2030 | 0.27023
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | ctrl | 2050 | 0.24445
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | lower | 2050 | 0.20267
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | L |  | upper | 2050 | 0.33779
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2015 | 0.01729
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2020 | 0.01729
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | lower | 2020 | 0.01
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | upper | 2020 | 0.11
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2030 | 0.01729
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2050 | 0.01729
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | lower | 2050 | 0.01
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | upper | 2050 | 0.13
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2015 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | lower | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | upper | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2030 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | ctrl | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, N] |  | upper | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 34000
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 33100
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 28300
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 38300
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 31300
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 28300
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 21900
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 37500
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2015 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | lower | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | upper | 2020 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2030 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | ctrl | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, N] |  | upper | 2050 | 1
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2015 | 0.004
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2020 | 0.003901
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | lower | 2020 | 0.0034
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | upper | 2020 | 0.0046
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2030 | 0.0037103
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | ctrl | 2050 | 0.0033564
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | lower | 2050 | 0.0027827
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | L |  | upper | 2050 | 0.0046378
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | ctrl | 2015 | 0.74133
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | ctrl | 2020 | 0.72298
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | lower | 2020 | 0.63013
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | upper | 2020 | 0.85253
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | ctrl | 2030 | 0.68764
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | ctrl | 2050 | 0.62204
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | lower | 2050 | 0.51573
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, L] | 1 | upper | 2050 | 0.90991
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2015 | 0.056599
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2020 | 0.056599
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | lower | 2020 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | upper | 2020 | 0.058575
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2030 | 0.056599
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | ctrl | 2050 | 0.056599
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | lower | 2050 | 0
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | D |  | upper | 2050 | 0.058575
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2015 | 1.86
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2020 | 1.98
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | lower | 2020 | 1.84
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | upper | 2020 | 2.09
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2030 | 2.65
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | ctrl | 2050 | 2.98
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | lower | 2050 | 2.78
09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | M |  | upper | 2050 | 3.15
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, J] |  | ctrl | 2015 | 0.020956
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, J] |  | ctrl | 2020 | 0.020956
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, J] |  | lower | 2020 | 0.018096
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, J] |  | upper | 2020 | 0.02338
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, J] |  | ctrl | 2030 | 0.020956
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, J] |  | ctrl | 2050 | 0.020956
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, J] |  | lower | 2050 | 0.014478
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | [C, J] |  | upper | 2050 | 0.023357
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 1.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 1.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2015 | 6.194
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2020 | 6.194
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | lower | 2020 | 5.3378
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | upper | 2020 | 6.2166
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2030 | 6.194
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | ctrl | 2050 | 6.194
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | lower | 2050 | 5.3378
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | A | 1 | upper | 2050 | 6.2226
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 3.4
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 4.6
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 3
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.24217
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.24217
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.20584
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.2785
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.24217
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.24217
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.18163
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.30271
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 20
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 35
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 20
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 35
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2015 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2020 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | lower | 2020 | 0.88
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | upper | 2020 | 1.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2030 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | ctrl | 2050 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | lower | 2050 | 0.88
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [B, C] | 1 | upper | 2050 | 1.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2015 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2020 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | lower | 2020 | 0.88
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | upper | 2020 | 1.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2030 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | ctrl | 2050 | 1.0323
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | lower | 2050 | 0.88
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [B, C] | 1 | upper | 2050 | 1.04
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | ctrl | 2015 | 16
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | ctrl | 2020 | 11
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | lower | 2020 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | upper | 2020 | 16
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | ctrl | 2030 | 8
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | ctrl | 2050 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | lower | 2050 | 2
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | G | 1 | upper | 2050 | 16
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | ctrl | 2015 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | ctrl | 2020 | 3
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | lower | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | upper | 2020 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | ctrl | 2030 | 2
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | ctrl | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | lower | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | G | 1 | upper | 2050 | 4
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | ctrl | 2015 | 90
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | ctrl | 2020 | 70
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | lower | 2020 | 40
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | upper | 2020 | 90
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | ctrl | 2030 | 70
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | ctrl | 2050 | 70
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | lower | 2050 | 20
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | G | 1 | upper | 2050 | 70
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | ctrl | 2015 | 2
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | ctrl | 2020 | 0.3
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | lower | 2020 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | upper | 2020 | 2
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | ctrl | 2030 | 0.3
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | ctrl | 2050 | 0.3
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | lower | 2050 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | G | 1 | upper | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2015 | 0.9545
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2020 | 0.9636
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | lower | 2020 | 0.909
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | upper | 2020 | 0.99818
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2030 | 0.9909
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | ctrl | 2050 | 0.99818
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | lower | 2050 | 0.9545
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | G | 1 | upper | 2050 | 0.99909
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2015 | 0.43591
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2020 | 0.42512
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, K] |  | lower | 2020 | 0.37052
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, K] |  | upper | 2020 | 0.55008
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2030 | 0.40433
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2050 | 0.36576
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, K] |  | lower | 2050 | 0.30325
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | [F, K] |  | upper | 2050 | 0.5542
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2015 | 0.46174
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2020 | 0.45031
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, K] |  | lower | 2020 | 0.39248
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, K] |  | upper | 2020 | 0.531
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2030 | 0.42829
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2050 | 0.38744
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, K] |  | lower | 2050 | 0.32122
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | [F, K] |  | upper | 2050 | 0.53537
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2015 | 1.3202
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2020 | 1.446
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, L] |  | lower | 2020 | 1.4294
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, L] |  | upper | 2020 | 1.708
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2030 | 2.1166
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2050 | 2.4519
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, L] |  | lower | 2050 | 2.4219
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [F, L] |  | upper | 2050 | 2.8962
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2015 | 0.66708
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2020 | 0.66708
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, L] |  | lower | 2020 | 0.49204
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, L] |  | upper | 2020 | 0.87748
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2030 | 0.66708
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2050 | 0.66708
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, L] |  | lower | 2050 | 0.43373
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | [F, L] |  | upper | 2050 | 0.94489
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2015 | 52300
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2020 | 50800
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | lower | 2020 | 43400
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | upper | 2020 | 59600
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2030 | 47900
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2050 | 42900
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | lower | 2050 | 32800
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | upper | 2050 | 55700
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2015 | 0.89764
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2020 | 0.87542
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, K] |  | lower | 2020 | 0.763
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, K] |  | upper | 2020 | 1.0811
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2030 | 0.83263
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2050 | 0.7532
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, K] |  | lower | 2050 | 0.62447
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, K] |  | upper | 2050 | 1.0896
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2015 | 1.9873
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2020 | 2.113
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, L] |  | lower | 2020 | 1.9215
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, L] |  | upper | 2020 | 2.5855
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2030 | 2.7836
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, L] |  | ctrl | 2050 | 3.1189
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, L] |  | lower | 2050 | 2.8556
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | [F, L] |  | upper | 2050 | 3.8411
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2015 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | lower | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | upper | 2020 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2030 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | ctrl | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | lower | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | E | 1 | upper | 2050 | 0.5
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2015 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2020 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | lower | 2020 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | upper | 2020 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2030 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | ctrl | 2050 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | lower | 2050 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | E | 1 | upper | 2050 | 0.1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2015 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2020 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | lower | 2020 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | upper | 2020 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2030 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | ctrl | 2050 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | lower | 2050 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | 1 | upper | 2050 | 0.25
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.45
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.43886
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.3825
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.56786
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.41741
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.37759
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.31305
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.57212
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.47667
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.46487
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.40517
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.54817
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.44214
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.39997
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.33161
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.55268
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2015 | 0.017669
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2020 | 0.017669
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | lower | 2020 | 0.01
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | upper | 2020 | 0.15
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2030 | 0.017669
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | ctrl | 2050 | 0.017669
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | lower | 2050 | 0.01
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | D | 1 | upper | 2050 | 0.15
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, M] |  | ctrl | 2015 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, M] |  | ctrl | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, M] |  | lower | 2020 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, M] |  | upper | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, M] |  | ctrl | 2030 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, M] |  | ctrl | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, M] |  | lower | 2050 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | [D, M] |  | upper | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 54000
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 52400
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 44800
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 61600
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 49400
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 44200
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 33900
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 57500
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, M] |  | ctrl | 2015 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, M] |  | ctrl | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, M] |  | lower | 2020 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, M] |  | upper | 2020 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, M] |  | ctrl | 2030 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, M] |  | ctrl | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, M] |  | lower | 2050 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | [D, M] |  | upper | 2050 | 1
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.08
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.07802
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.068
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.092
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.074206
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.067127
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.055654
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.092757
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [I, K] | 1 | ctrl | 2015 | 0.92667
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [I, K] | 1 | ctrl | 2020 | 0.90373
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [I, K] | 1 | lower | 2020 | 0.78767
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [I, K] | 1 | upper | 2020 | 1.116
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [I, K] | 1 | ctrl | 2030 | 0.85955
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [I, K] | 1 | ctrl | 2050 | 0.77756
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [I, K] | 1 | lower | 2050 | 0.64466
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [I, K] | 1 | upper | 2050 | 1.1248
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, L] |  | ctrl | 2015 | 0.088886
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, L] |  | ctrl | 2020 | 0.088886
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, L] |  | lower | 2020 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, L] |  | upper | 2020 | 0.090904
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, L] |  | ctrl | 2030 | 0.088886
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, L] |  | ctrl | 2050 | 0.088886
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, L] |  | lower | 2050 | 0
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Output of recovered condensate [t/MWh_i] | Output of recovered condensate |  | t/MWh_i |  | [D, L] |  | upper | 2050 | 0.090904
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 2.05
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 2.18
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 1.99
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 2.3
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 2.87
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 3.22
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 2.96
09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 3.42
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015 | 0.44
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020 | 0.42
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020 | 0.41
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030 | 0.42
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050 | 0.4
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050 | 0.43
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050 | 0.44
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015 | 0.14
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020 | 0.14
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2020 | 0.13
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2020 | 0.13
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030 | 0.14
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050 | 0.13
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2050 | 0.13
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2050 | 0.14
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.408
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.409
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.378
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.41
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.41
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.394
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.385
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.414
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.43
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.43
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.398
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.431
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.432
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.414
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.404
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.436
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 257.7
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 258.2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 238.8
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 258.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 259.7
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 248.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 242.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 261.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.8
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2015 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2020 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2020 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2020 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2030 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | ctrl | 2050 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | lower | 2050 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  | 1 | upper | 2050 | 0.06
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 25
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 8
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 30
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 20
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 30
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 20
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 10
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 20
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2015 | 0.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2020 | 0.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2020 | 0.1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2020 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2030 | 0.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | ctrl | 2050 | 0.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | lower | 2050 | 0.1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  | F | [1, 2, 3] | upper | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2015 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2020 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | lower | 2020 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | upper | 2020 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2030 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | ctrl | 2050 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | lower | 2050 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  | F | [1, 2, 3] | upper | 2050 | 0.975
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 1.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.9
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 1.5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 1.4
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 1.4
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 2.1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 0.9
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 0.8
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 0.9
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 0.8
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 0.8
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015 | 70000
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020 | 69000
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020 | 66000
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020 | 80000
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030 | 64000
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050 | 62000
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050 | 57000
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050 | 79000
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 2.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 2.5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 2.4
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 3.1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 2.4
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 2.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 2.2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 3.3
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 2.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 2.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 2.8
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 2.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 2.6
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 2.7
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 2.7
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 2.5
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2020 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2020 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | lower | 2050 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | upper | 2050 | 12
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.45
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.04
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2015 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2020 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | lower | 2020 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | upper | 2020 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2030 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | ctrl | 2050 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | lower | 2050 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | [E, G] | 1 | upper | 2050 | 2
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.69
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.67
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.59
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.84
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.63
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.59
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.55
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.92
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.42
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.41
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.35
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.48
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.4
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.36
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.33
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.52
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.041
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | ctrl | 2015 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | ctrl | 2020 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | lower | 2020 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | upper | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | ctrl | 2030 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | ctrl | 2050 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | lower | 2050 | 0
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | upper | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 30200
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 29500
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 26400
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 34400
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 27900
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 25500
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 23200
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 34200
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | ctrl | 2015 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | ctrl | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | lower | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | upper | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | ctrl | 2030 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | ctrl | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | lower | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | upper | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 1.1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 1.08
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.94
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 1.32
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 1.02
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.94
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.88
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 1.44
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 1
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 1.11
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 1.11
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 1.11
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 1.11
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 1.11
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 1.11
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 1.11
09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 1.11
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015 | 0.59
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020 | 0.59
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2020 | 0.57
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2020 | 0.52
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030 | 0.59
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050 | 0.52
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | lower | 2050 | 0.59
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  |  |  | upper | 2050 | 0.53
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2015 | 5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2020 | 5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2020 | 5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2030 | 5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | ctrl | 2050 | 5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | lower | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 1 | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2015 | 0.17
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2020 | 0.17
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | lower | 2020 | 0.17
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | upper | 2020 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2030 | 0.17
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | ctrl | 2050 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | lower | 2050 | 0.17
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  | I |  | upper | 2050 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2015 | 0.423
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2020 | 0.425
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2020 | 0.412
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2020 | 0.427
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2030 | 0.426
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | ctrl | 2050 | 0.426
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | lower | 2050 | 0.418
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | [A, H] | 1 | upper | 2050 | 0.433
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2015 | 0.445
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2020 | 0.447
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2020 | 0.434
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2020 | 0.449
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2030 | 0.448
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | ctrl | 2050 | 0.448
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | lower | 2050 | 0.44
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | [A, H] | 1 | upper | 2050 | 0.455
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.03
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2015 | 356.4
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2020 | 357.6
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2020 | 347.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2020 | 359.4
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2030 | 358.7
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | ctrl | 2050 | 358.4
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | lower | 2050 | 351.7
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A |  | upper | 2050 | 364.4
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015 | 3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020 | 2.6
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020 | 3.5
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050 | 2.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050 | 3.8
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2015 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2030 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | ctrl | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | lower | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  |  |  | upper | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2020 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2020 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | lower | 2050 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | upper | 2050 | 25
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2015 | 20
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2020 | 20
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | lower | 2020 | 10
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | upper | 2020 | 30
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2030 | 20
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | ctrl | 2050 | 10
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | lower | 2050 | 10
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  | [C, F] | [1, 2] | upper | 2050 | 20
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 0.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 0.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 0.1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 0.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 0.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 0.1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2015 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2020 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | lower | 2020 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | upper | 2020 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2030 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | ctrl | 2050 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | lower | 2050 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | [1, 2] | upper | 2050 | 0.975
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 1.34
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 1.3
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2020 | 1.16
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1.58
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 1.23
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 1.16
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | lower | 2050 | 1.08
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.7
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2015 | 0.88
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2020 | 0.86
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2020 | 0.77
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2030 | 0.81
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | ctrl | 2050 | 0.74
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | lower | 2050 | 0.71
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | K |  | upper | 2050 | 1.08
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2015 | 57000
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2020 | 55000
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2020 | 51000
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2020 | 63000
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2030 | 52000
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | ctrl | 2050 | 49000
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | lower | 2050 | 46000
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 |  |  | upper | 2050 | 63000
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2015 | 2.22
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 2.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2020 | 1.93
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2020 | 2.59
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2030 | 2.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2050 | 1.9
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | lower | 2050 | 1.8
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | upper | 2050 | 2.78
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2015 | 1.1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2020 | 1.1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2020 | 1.2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2020 | 1.1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2030 | 1.1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | ctrl | 2050 | 1.1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | lower | 2050 | 1.2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | L |  | upper | 2050 | 1.1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2015 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2020 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | lower | 2020 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | upper | 2020 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2030 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | ctrl | 2050 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | lower | 2050 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | 1 | upper | 2050 | 12
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2015 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2020 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | lower | 2020 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | upper | 2020 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2030 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | ctrl | 2050 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | lower | 2050 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 1 | upper | 2050 | 0.15
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050 | 0.02
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2015 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2020 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2030 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | ctrl | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | lower | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D | 1 | upper | 2050 | 0.04
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2015 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2020 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2020 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2020 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2030 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | ctrl | 2050 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | lower | 2050 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | 1 | upper | 2050 | 2
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.59
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.58
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.51
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.71
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.55
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.52
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.48
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (equipment) [2015-MEUR/MW_i] | Nominal investment | equipment | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.77
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2015 | 0.39
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2020 | 0.38
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2020 | 0.33
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2020 | 0.45
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2030 | 0.36
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | ctrl | 2050 | 0.33
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | lower | 2050 | 0.31
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (installation) [2015-MEUR/MW_i] | Nominal investment | installation | MEUR/MW_i | 2015 | K |  | upper | 2050 | 0.49
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2015
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2020
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2020
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2020 | 0.036
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2030
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | ctrl | 2050 | 0.036
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | lower | 2050
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Additional heat potential with heat pumps (of thermal input) [] | Additional heat potential with heat pumps | of thermal input | [] |  | C | 1 | upper | 2050 | 0.036
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | lower | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | ctrl | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | lower | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Combustion air humidification | Combustion air humidification |  |  |  | M |  | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2015 | 25200
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2020 | 24600
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2020 | 22200
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2020 | 28300
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2030 | 23500
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | ctrl | 2050 | 21900
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | lower | 2050 | 20000
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fixed O&M (*total) [2015-EUR/MW_i/y] | Fixed O&M | *total | EUR/MW_i/y | 2015 |  |  | upper | 2050 | 28600
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | ctrl | 2015 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | ctrl | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | lower | 2020 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | ctrl | 2030 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | ctrl | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | lower | 2050 | 0
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Flue gas condensation | Flue gas condensation |  |  |  | M |  | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2015 | 0.0025
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2020 | 0.0025
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2020 | 0.0025
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2020 | 0.0025
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2030 | 0.0025
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | ctrl | 2050 | 0.0025
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | lower | 2050 | 0.0025
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Fuel storage specific cost in excess of 2 days [2015-MEUR/MW_i/storage day] | Fuel storage specific cost in excess of 2 days |  | MEUR/MW_i/storage day | 2015 | K |  | upper | 2050 | 0.0025
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2015 | 0.99
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2020 | 0.96
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2020 | 0.84
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2020 | 1.16
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2030 | 0.92
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | ctrl | 2050 | 0.85
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | lower | 2050 | 0.79
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Nominal investment (*total) [2015-MEUR/MW_i] | Nominal investment | *total | MEUR/MW_i | 2015 | [J, K] | 1 | upper | 2050 | 1.26
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2015 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2020 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2030 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | ctrl | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | lower | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Steam reheat | Steam reheat |  |  |  | M |  | upper | 2050 | 1
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2015 | 0.51
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2020 | 0.51
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2020 | 0.51
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2020 | 0.51
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2030 | 0.51
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | ctrl | 2050 | 0.51
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | lower | 2050 | 0.51
09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Technology-specific data | Variable O&M (*total) [2015-EUR/MWh_i] | Variable O&M | *total | EUR/MWh_i | 2015 | L |  | upper | 2050 | 0.51
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | 1 | ctrl | 2015 | 0.4
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | 1 | ctrl | 2020 | 0.3
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | B | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 1 | ctrl | 2015 | 0.2
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 1 | ctrl | 2020 | 0.22
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  | A | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2015 | 0.04
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2020 | 0.03
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 1 | ctrl | 2015 | 0.037
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 1 | ctrl | 2020 | 0.04
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Technology-specific data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  | 1 | ctrl | 2015 | 0.12
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Technology-specific data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  | 1 | ctrl | 2020 | 0.12
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Technology-specific data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Technology-specific data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 1 | ctrl | 2015 | 3
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 1 | ctrl | 2020 | 2
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2015 | 15
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2020 | 15
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2015 | 1
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2020 | 1
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | CH4 [ppm] | CH4 |  | ppm |  |  | 1 | ctrl | 2015 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | CH4 [ppm] | CH4 |  | ppm |  |  | 1 | ctrl | 2020 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | CH4 [ppm] | CH4 |  | ppm |  |  | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | CH4 [ppm] | CH4 |  | ppm |  |  | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | N2O [ppm] | N2O |  | ppm |  |  | 1 | ctrl | 2015 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | N2O [ppm] | N2O |  | ppm |  |  | 1 | ctrl | 2020 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | N2O [ppm] | N2O |  | ppm |  |  | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | N2O [ppm] | N2O |  | ppm |  |  | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | NOX [ppm] | NOX |  | ppm |  |  | 1 | ctrl | 2015 | 130
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | NOX [ppm] | NOX |  | ppm |  |  | 1 | ctrl | 2020 | 100
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | NOX [ppm] | NOX |  | ppm |  |  | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | NOX [ppm] | NOX |  | ppm |  |  | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 1 | ctrl | 2015 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 1 | ctrl | 2020 | 0
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, E] | 1 | ctrl | 2015 | 32000
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, E] | 1 | ctrl | 2020 | 32000
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, E] | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | [D, E] | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 1 | ctrl | 2015 | 5
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 1 | ctrl | 2020 | 3.8
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 1 | ctrl | 2050
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [D, E] | 1 | ctrl | 2015 | 26
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [D, E] | 1 | ctrl | 2020 | 21
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [D, E] | 1 | ctrl | 2030
10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 | [D, E] | 1 | ctrl | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [C, L] | [, *, *, *] | ctrl | 2015
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [C, L] | [, *, *, *] | ctrl | 2020 | 1.6667
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [C, L] | [, *, *, *] | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [C, L] | [, *, *, *] | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [C, L] | [, *, *, *] | ctrl | 2030 | 1.6129
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [C, L] | [, *, *, *] | ctrl | 2050 | 1.6129
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [C, L] | [, *, *, *] | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | [C, L] | [, *, *, *] | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | [3, *, *, *] | ctrl | 2015 | 0.56
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | [3, *, *, *] | ctrl | 2020 | 0.58
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | [3, *, *, *] | lower | 2020 | 0.52
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | [3, *, *, *] | upper | 2020 | 0.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | [3, *, *, *] | ctrl | 2030 | 0.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | [3, *, *, *] | ctrl | 2050 | 0.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | [3, *, *, *] | lower | 2050 | 0.56
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | B | [3, *, *, *] | upper | 2050 | 0.62
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  |  | ctrl | 2015 | 0.56
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  |  | ctrl | 2020 | 0.58
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  |  | ctrl | 2030 | 0.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  |  | ctrl | 2050 | 0.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | [3, *, *, *] | ctrl | 2015 | 0.25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | [3, *, *, *] | ctrl | 2020 | 2.5
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | [3, *, *, *] | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | [3, *, *, *] | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | [3, *, *, *] | ctrl | 2030 | 10
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | [3, *, *, *] | ctrl | 2050 | 20
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | [3, *, *, *] | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A | [3, *, *, *] | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [6, 6, *, *] | ctrl | 2015 | 15
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [6, 6, *, *] | ctrl | 2020 | 20
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [6, 6, *, *] | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [6, 6, *, *] | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [6, 6, *, *] | ctrl | 2030 | 20
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [6, 6, *, *] | ctrl | 2050 | 20
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [6, 6, *, *] | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | [6, 6, *, *] | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 7 | ctrl | 2015 | 1.25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 7 | ctrl | 2020 | 1.25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 7 | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 7 | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 7 | ctrl | 2030 | 1.25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 7 | ctrl | 2050 | 1.25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 7 | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  | F | 7 | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | * | ctrl | 2015
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | * | ctrl | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | * | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | * | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | * | ctrl | 2030
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | * | ctrl | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | * | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | F | * | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 3 | ctrl | 2015 | 1.3
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 3 | ctrl | 2020 | 1.4
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 3 | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 3 | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 3 | ctrl | 2030 | 1.5
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 3 | ctrl | 2050 | 1.6
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 3 | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | 3 | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 3 | ctrl | 2015 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 3 | ctrl | 2020 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 3 | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 3 | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 3 | ctrl | 2030 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 3 | ctrl | 2050 | 1
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 3 | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  | 3 | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | G |  | ctrl | 2015 | 6.64
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | G |  | ctrl | 2020 | 2.31
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | G |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | G |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | G |  | ctrl | 2030 | 1.2
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | G |  | ctrl | 2050 | 0.464
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | G |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | G |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | G |  | ctrl | 2015 | 1.66
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | G |  | ctrl | 2020 | 0.99
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | G |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | G |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | G |  | ctrl | 2030 | 0.8
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | G |  | ctrl | 2050 | 0.336
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | G |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | G |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | K | 8 | ctrl | 2015 | 415000
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | K | 8 | ctrl | 2020 | 165000
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | K | 8 | lower | 2020 | 135000
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | K | 8 | upper | 2020 | 290000
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | K | 8 | ctrl | 2030 | 100000
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | K | 8 | ctrl | 2050 | 40000
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | K | 8 | lower | 2050 | 20000
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | K | 8 | upper | 2050 | 65000
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [G, H, I, J] | [8, 13] | ctrl | 2015 | 8.3
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [G, H, I, J] | [8, 13] | ctrl | 2020 | 3.3
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [G, H, I, J] | [8, 13] | lower | 2020 | 2.7
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [G, H, I, J] | [8, 13] | upper | 2020 | 5.8
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [G, H, I, J] | [8, 13] | ctrl | 2030 | 2
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [G, H, I, J] | [8, 13] | ctrl | 2050 | 0.8
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [G, H, I, J] | [8, 13] | lower | 2050 | 0.4
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [G, H, I, J] | [8, 13] | upper | 2050 | 1.3
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | ctrl | 2015
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | ctrl | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | ctrl | 2030
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | ctrl | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Startup cost [2015-EUR/MW_e/startup] | Startup cost |  | EUR/MW_e/startup | 2015 |  |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2015
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2030
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [*, *, *, *] | ctrl | 2015 | 25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [*, *, *, *] | ctrl | 2020 | 25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [*, *, *, *] | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [*, *, *, *] | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [*, *, *, *] | ctrl | 2030 | 25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [*, *, *, *] | ctrl | 2050 | 25
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [*, *, *, *] | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | E | [*, *, *, *] | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.7
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.7
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.7
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.7
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2015
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E |  | ctrl | 2015 | 0.025
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E |  | ctrl | 2020 | 0.025
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E |  | lower | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E |  | upper | 2020
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E |  | ctrl | 2030 | 0.025
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E |  | ctrl | 2050 | 0.025
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E |  | lower | 2050
11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | E |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | D |  | ctrl | 2015
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | D |  | ctrl | 2020 | 1.25
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | D |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | D |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | D |  | ctrl | 2030 | 1.25
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | D |  | ctrl | 2050 | 1.25
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | D |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cb coefficient (50°C/100°C) | Cb coefficient | 50°C/100°C |  |  | D |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2015
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2030
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | ctrl | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Cv coefficient (50°C/100°C) | Cv coefficient | 50°C/100°C |  |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 5] | ctrl | 2015 | 0.45
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 5] | ctrl | 2020 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 5] | lower | 2020 | 0.45
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 5] | upper | 2020 | 0.52
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 5] | ctrl | 2030 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 5] | ctrl | 2050 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 5] | lower | 2050 | 0.46
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, annual average) [] | Electrical efficiency | net, annual average | [] |  | A | [3, 5] | upper | 2050 | 0.53
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2015 | 0.45
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2020 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2030 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | ctrl | 2050 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Electrical efficiency (net, name plate) [] | Electrical efficiency | net, name plate | [] |  |  | 5 | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.001
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.001
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.001
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.001
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 5 | ctrl | 2015 | 0.05
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 5 | ctrl | 2020 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 5 | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 5 | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 5 | ctrl | 2030 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 5 | ctrl | 2050 | 2
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 5 | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | 5 | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2015
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2020 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2030 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | ctrl | 2050 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2015 | 10
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2020 | 10
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2030 | 10
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2050 | 10
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2015 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 4 | ctrl | 2015 | 1.6
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 4 | ctrl | 2020 | 1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 4 | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 4 | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 4 | ctrl | 2030 | 0.8
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 4 | ctrl | 2050 | 0.6
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 4 | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 4 | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 4 | ctrl | 2015 | 0.3
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 4 | ctrl | 2020 | 0.3
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 4 | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 4 | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 4 | ctrl | 2030 | 0.3
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 4 | ctrl | 2050 | 0.2
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 4 | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 |  | 4 | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | C |  | ctrl | 2015 | 95000
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | C |  | ctrl | 2020 | 65000
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | C |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | C |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | C |  | ctrl | 2030 | 55000
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | C |  | ctrl | 2050 | 40000
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | C |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | C |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | B | [3, 4] | ctrl | 2015 | 1.9
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | B | [3, 4] | ctrl | 2020 | 1.3
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | B | [3, 4] | lower | 2020 | 1.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | B | [3, 4] | upper | 2020 | 1.6
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | B | [3, 4] | ctrl | 2030 | 1.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | B | [3, 4] | ctrl | 2050 | 0.8
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | B | [3, 4] | lower | 2050 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | B | [3, 4] | upper | 2050 | 0.9
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2015
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2030
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2015
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2030
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.1
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015 | 0.5
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020 | 0.25
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030 | 0.025
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050 | 0.0125
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2015
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2015 | 0.01
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020 | 0.01
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030 | 0.01
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050 | 0.01
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Technology-specific data | Minimum load efficiency [] | Minimum load efficiency |  | [] |  |  | 5 | ctrl | 2015 | 0.3
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Technology-specific data | Minimum load efficiency [] | Minimum load efficiency |  | [] |  |  | 5 | ctrl | 2020 | 0.35
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Technology-specific data | Minimum load efficiency [] | Minimum load efficiency |  | [] |  |  | 5 | lower | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Technology-specific data | Minimum load efficiency [] | Minimum load efficiency |  | [] |  |  | 5 | upper | 2020
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Technology-specific data | Minimum load efficiency [] | Minimum load efficiency |  | [] |  |  | 5 | ctrl | 2030 | 0.35
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Technology-specific data | Minimum load efficiency [] | Minimum load efficiency |  | [] |  |  | 5 | ctrl | 2050 | 0.35
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Technology-specific data | Minimum load efficiency [] | Minimum load efficiency |  | [] |  |  | 5 | lower | 2050
12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Technology-specific data | Minimum load efficiency [] | Minimum load efficiency |  | [] |  |  | 5 | upper | 2050
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, L] | 3 | ctrl | 2015 | 3100
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, L] | 3 | ctrl | 2020 | 3400
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, L] | 3 | lower | 2020 | 2000
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, L] | 3 | upper | 2020 | 4000
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, L] | 3 | ctrl | 2030 | 3600
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, L] | 3 | ctrl | 2040 | 3700
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, L] | 3 | ctrl | 2050 | 3800
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, L] | 3 | lower | 2050 | 2000
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, L] | 3 | upper | 2050 | 4500
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | E | 4 | ctrl | 2015 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | E | 4 | ctrl | 2020 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | E | 4 | lower | 2020 | 1
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | E | 4 | upper | 2020 | 3
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | E | 4 | ctrl | 2030 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | E | 4 | ctrl | 2040 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | E | 4 | ctrl | 2050 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | E | 4 | lower | 2050 | 1
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | E | 4 | upper | 2050 | 3
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | B | 4 | ctrl | 2015 | 0.03
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | B | 4 | ctrl | 2020 | 0.025
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | B | 4 | lower | 2020 | 0.01
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | B | 4 | upper | 2020 | 0.05
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | B | 4 | ctrl | 2030 | 0.02
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | B | 4 | ctrl | 2040 | 0.018
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | B | 4 | ctrl | 2050 | 0.015
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | B | 4 | lower | 2050 | 0.01
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | B | 4 | upper | 2050 | 0.05
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A1 | 3 | ctrl | 2015 | 3.1
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A1 | 3 | ctrl | 2020 | 4.2
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A1 | 3 | lower | 2020 | 2
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A1 | 3 | upper | 2020 | 6
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A1 | 3 | ctrl | 2030 | 5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A1 | 3 | ctrl | 2040 | 5.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A1 | 3 | ctrl | 2050 | 6
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A1 | 3 | lower | 2050 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  | A1 | 3 | upper | 2050 | 8
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 4 | ctrl | 2015 | 0.15643
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 4 | ctrl | 2020 | 0.15643
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 4 | lower | 2020 | 0.052143
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 4 | upper | 2020 | 0.26071
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 4 | ctrl | 2030 | 0.15643
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 4 | ctrl | 2040 | 0.15643
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 4 | ctrl | 2050 | 0.15643
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 4 | lower | 2050 | 0.052143
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | C | 4 | upper | 2050 | 0.26071
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | F |  | ctrl | 2015
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | F |  | ctrl | 2020
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | F |  | lower | 2020
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | F |  | upper | 2020
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | F |  | ctrl | 2030
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | F |  | ctrl | 2040
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | F |  | ctrl | 2050
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | F |  | lower | 2050
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | F |  | upper | 2050
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | 14 | ctrl | 2015 | 25
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | 14 | ctrl | 2020 | 27
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | 14 | lower | 2020 | 25
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | 14 | upper | 2020 | 35
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | 14 | ctrl | 2030 | 30
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | 14 | ctrl | 2040 | 30
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | 14 | ctrl | 2050 | 30
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | 14 | lower | 2050 | 25
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | D | 14 | upper | 2050 | 40
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 25 | ctrl | 2015 | 0.89
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 25 | ctrl | 2020 | 0.7146
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 25 | lower | 2020 | 0.57168
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 25 | upper | 2020 | 0.85752
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 25 | ctrl | 2030 | 0.64314
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 25 | ctrl | 2040 | 0.59169
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 25 | ctrl | 2050 | 0.57883
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 25 | lower | 2050 | 0.46306
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 |  | 25 | upper | 2050 | 0.69459
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 25 | ctrl | 2015 | 0.115
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 25 | ctrl | 2020 | 0.0909
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 25 | lower | 2020 | 0.07272
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 25 | upper | 2020 | 0.10908
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 25 | ctrl | 2030 | 0.08181
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 25 | ctrl | 2040 | 0.075265
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 25 | ctrl | 2050 | 0.073629
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 25 | lower | 2050 | 0.058903
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | M | 25 | upper | 2050 | 0.088355
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (decommissioning of existing turbines) [2015-MEUR/MW_e] | Nominal investment | decommissioning of existing turbines | MEUR/MW_e | 2015 |  | 25 | ctrl | 2015 | 0.0399
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (decommissioning of existing turbines) [2015-MEUR/MW_e] | Nominal investment | decommissioning of existing turbines | MEUR/MW_e | 2015 |  | 25 | ctrl | 2020 | 0.036
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (decommissioning of existing turbines) [2015-MEUR/MW_e] | Nominal investment | decommissioning of existing turbines | MEUR/MW_e | 2015 |  | 25 | lower | 2020 | 0.0288
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (decommissioning of existing turbines) [2015-MEUR/MW_e] | Nominal investment | decommissioning of existing turbines | MEUR/MW_e | 2015 |  | 25 | upper | 2020 | 0.0432
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (decommissioning of existing turbines) [2015-MEUR/MW_e] | Nominal investment | decommissioning of existing turbines | MEUR/MW_e | 2015 |  | 25 | ctrl | 2030 | 0.036
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (decommissioning of existing turbines) [2015-MEUR/MW_e] | Nominal investment | decommissioning of existing turbines | MEUR/MW_e | 2015 |  | 25 | ctrl | 2040 | 0.036
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (decommissioning of existing turbines) [2015-MEUR/MW_e] | Nominal investment | decommissioning of existing turbines | MEUR/MW_e | 2015 |  | 25 | ctrl | 2050 | 0.036
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (decommissioning of existing turbines) [2015-MEUR/MW_e] | Nominal investment | decommissioning of existing turbines | MEUR/MW_e | 2015 |  | 25 | lower | 2050 | 0.0288
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (decommissioning of existing turbines) [2015-MEUR/MW_e] | Nominal investment | decommissioning of existing turbines | MEUR/MW_e | 2015 |  | 25 | upper | 2050 | 0.0432
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 |  | 25 | ctrl | 2015 | 0.063145
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 |  | 25 | ctrl | 2020 | 0.053275
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 |  | 25 | lower | 2020 | 0.04262
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 |  | 25 | upper | 2020 | 0.06393
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 |  | 25 | ctrl | 2030 | 0.050611
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 |  | 25 | ctrl | 2040 | 0.050611
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 |  | 25 | ctrl | 2050 | 0.050611
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 |  | 25 | lower | 2050 | 0.040489
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 |  | 25 | upper | 2050 | 0.060734
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [2015-MEUR/MW_e] | Nominal investment | other, i.e. compensation of neighbours | MEUR/MW_e | 2015 | I | [25, 26] | ctrl | 2015 | 0.133
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [2015-MEUR/MW_e] | Nominal investment | other, i.e. compensation of neighbours | MEUR/MW_e | 2015 | I | [25, 26] | ctrl | 2020 | 0.139
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [2015-MEUR/MW_e] | Nominal investment | other, i.e. compensation of neighbours | MEUR/MW_e | 2015 | I | [25, 26] | lower | 2020 | 0.1112
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [2015-MEUR/MW_e] | Nominal investment | other, i.e. compensation of neighbours | MEUR/MW_e | 2015 | I | [25, 26] | upper | 2020 | 0.1668
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [2015-MEUR/MW_e] | Nominal investment | other, i.e. compensation of neighbours | MEUR/MW_e | 2015 | I | [25, 26] | ctrl | 2030 | 0.139
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [2015-MEUR/MW_e] | Nominal investment | other, i.e. compensation of neighbours | MEUR/MW_e | 2015 | I | [25, 26] | ctrl | 2040 | 0.139
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [2015-MEUR/MW_e] | Nominal investment | other, i.e. compensation of neighbours | MEUR/MW_e | 2015 | I | [25, 26] | ctrl | 2050 | 0.139
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [2015-MEUR/MW_e] | Nominal investment | other, i.e. compensation of neighbours | MEUR/MW_e | 2015 | I | [25, 26] | lower | 2050 | 0.1112
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (other, i.e. compensation of neighbours) [2015-MEUR/MW_e] | Nominal investment | other, i.e. compensation of neighbours | MEUR/MW_e | 2015 | I | [25, 26] | upper | 2050 | 0.1668
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (land rent) [2015-MEUR/MW_e] | Nominal investment | land rent | MEUR/MW_e | 2015 |  | 25 | ctrl | 2015 | 0.085
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (land rent) [2015-MEUR/MW_e] | Nominal investment | land rent | MEUR/MW_e | 2015 |  | 25 | ctrl | 2020 | 0.085
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (land rent) [2015-MEUR/MW_e] | Nominal investment | land rent | MEUR/MW_e | 2015 |  | 25 | lower | 2020 | 0.068
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (land rent) [2015-MEUR/MW_e] | Nominal investment | land rent | MEUR/MW_e | 2015 |  | 25 | upper | 2020 | 0.102
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (land rent) [2015-MEUR/MW_e] | Nominal investment | land rent | MEUR/MW_e | 2015 |  | 25 | ctrl | 2030 | 0.085
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (land rent) [2015-MEUR/MW_e] | Nominal investment | land rent | MEUR/MW_e | 2015 |  | 25 | ctrl | 2040 | 0.085
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (land rent) [2015-MEUR/MW_e] | Nominal investment | land rent | MEUR/MW_e | 2015 |  | 25 | ctrl | 2050 | 0.085
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (land rent) [2015-MEUR/MW_e] | Nominal investment | land rent | MEUR/MW_e | 2015 |  | 25 | lower | 2050 | 0.068
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (land rent) [2015-MEUR/MW_e] | Nominal investment | land rent | MEUR/MW_e | 2015 |  | 25 | upper | 2050 | 0.102
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | I | [25, 26] | ctrl | 2015 | 25600
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | I | [25, 26] | ctrl | 2020 | 14000
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | I | [25, 26] | lower | 2020 | 11200
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | I | [25, 26] | upper | 2020 | 16800
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | I | [25, 26] | ctrl | 2030 | 12600
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | I | [25, 26] | ctrl | 2040 | 11592
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | I | [25, 26] | ctrl | 2050 | 11340
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | I | [25, 26] | lower | 2050 | 9072
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | I | [25, 26] | upper | 2050 | 13608
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [16, 2, 4] | ctrl | 2015 | 1.326
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [16, 2, 4] | ctrl | 2020 | 1.1188
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [16, 2, 4] | lower | 2020 | 0.77045
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [16, 2, 4] | upper | 2020 | 1.1557
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [16, 2, 4] | ctrl | 2030 | 1.0356
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [16, 2, 4] | ctrl | 2040 | 0.97757
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [16, 2, 4] | ctrl | 2050 | 0.96307
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [16, 2, 4] | lower | 2050 | 0.79557
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [16, 2, 4] | upper | 2050 | 1.1934
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2015 | 2.8
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2020 | 1.5
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | lower | 2020 | 1.2
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | upper | 2020 | 1.8
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2030 | 1.35
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2040 | 1.242
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2050 | 1.215
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | lower | 2050 | 0.972
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | upper | 2050 | 1.458
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2015
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2020
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | lower | 2020
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | upper | 2020
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2030
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2040
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | ctrl | 2050
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | lower | 2050
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G |  | upper | 2050
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2015
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2020
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | lower | 2020
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | upper | 2020
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2030
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2040
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | ctrl | 2050
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | lower | 2050
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G |  | upper | 2050
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Availability [] | Availability |  | [] |  |  |  | ctrl | 2015 | 0.967
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Availability [] | Availability |  | [] |  |  |  | ctrl | 2020 | 0.972
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Availability [] | Availability |  | [] |  |  |  | lower | 2020 | 0.989
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Availability [] | Availability |  | [] |  |  |  | upper | 2020 | 0.945
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Availability [] | Availability |  | [] |  |  |  | ctrl | 2030 | 0.977
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Availability [] | Availability |  | [] |  |  |  | ctrl | 2040 | 0.977
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Availability [] | Availability |  | [] |  |  |  | ctrl | 2050 | 0.982
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Availability [] | Availability |  | [] |  |  |  | lower | 2050 | 0.989
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Availability [] | Availability |  | [] |  |  |  | upper | 2050 | 0.945
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average capacity factor [] | Average capacity factor |  | [] |  |  | [4, 26] | ctrl | 2015 | 0.35388
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average capacity factor [] | Average capacity factor |  | [] |  |  | [4, 26] | ctrl | 2020 | 0.38813
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average capacity factor [] | Average capacity factor |  | [] |  |  | [4, 26] | lower | 2020 | 0.22831
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average capacity factor [] | Average capacity factor |  | [] |  |  | [4, 26] | upper | 2020 | 0.45662
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average capacity factor [] | Average capacity factor |  | [] |  |  | [4, 26] | ctrl | 2030 | 0.41096
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average capacity factor [] | Average capacity factor |  | [] |  |  | [4, 26] | ctrl | 2040 | 0.42237
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average capacity factor [] | Average capacity factor |  | [] |  |  | [4, 26] | ctrl | 2050 | 0.43379
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average capacity factor [] | Average capacity factor |  | [] |  |  | [4, 26] | lower | 2050 | 0.22831
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Average capacity factor [] | Average capacity factor |  | [] |  |  | [4, 26] | upper | 2050 | 0.5137
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | [4, 26] | ctrl | 2015 | 85
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | [4, 26] | ctrl | 2020 | 85
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | [4, 26] | lower | 2020 | 85
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | [4, 26] | upper | 2020 | 120
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | [4, 26] | ctrl | 2030 | 100
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | [4, 26] | ctrl | 2040 | 105
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | [4, 26] | ctrl | 2050 | 110
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | [4, 26] | lower | 2050 | 85
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Hub height [m] | Hub height |  | m |  |  | [4, 26] | upper | 2050 | 150
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | K | [4, 26] | ctrl | 2015 | 106
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | K | [4, 26] | ctrl | 2020 | 130
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | K | [4, 26] | lower | 2020 | 90
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | K | [4, 26] | upper | 2020 | 130
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | K | [4, 26] | ctrl | 2030 | 145
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | K | [4, 26] | ctrl | 2040 | 155
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | K | [4, 26] | ctrl | 2050 | 165
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | K | [4, 26] | lower | 2050 | 100
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | K | [4, 26] | upper | 2050 | 150
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  |  |  | ctrl | 2015 | 351.2854
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  |  |  | ctrl | 2020 | 316.4264
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  |  |  | lower | 2020 | 314.3801
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  |  |  | upper | 2020 | 452.0377
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  |  |  | ctrl | 2030 | 302.7918
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  |  |  | ctrl | 2040 | 291.4804
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  |  |  | ctrl | 2050 | 280.6038
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  |  |  | lower | 2050 | 190.9859
20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Technology-specific data | Specific power [W_e/m2] | Specific power |  | W_e/m2 |  |  |  | upper | 2050 | 452.7074
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, J] |  | ctrl | 2015 | 1600
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, J] |  | ctrl | 2020 | 1800
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, J] |  | lower | 2020 | 1000
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, J] |  | upper | 2020 | 2300
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, J] |  | ctrl | 2030 | 2000
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, J] |  | ctrl | 2050 | 2200
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, J] |  | lower | 2050 | 1000
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  | [A, J] |  | upper | 2050 | 2300
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015 | 1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020 | 0.5
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020 | 1.5
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050 | 0.5
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050 | 1.5
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2015 | 0.03
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2020 | 0.03
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2020 | 0.02
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2020 | 0.1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2030 | 0.03
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | ctrl | 2050 | 0.03
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | lower | 2050 | 0.02
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  |  | upper | 2050 | 0.1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2015 | 0.01
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2020 | 0.01
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2020 | 0.005
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2020 | 0.025
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2030 | 0.01
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | ctrl | 2050 | 0.01
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | lower | 2050 | 0.005
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  |  | upper | 2050 | 0.025
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2015 | 0.15643
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2020 | 0.15643
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | lower | 2020 | 0.052143
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | upper | 2020 | 0.26071
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2030 | 0.15643
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | ctrl | 2050 | 0.15643
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | lower | 2050 | 0.052143
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | B |  | upper | 2050 | 0.26071
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | C |  | ctrl | 2015 | 0.8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | C |  | ctrl | 2020 | 0.8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | C |  | lower | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | C |  | upper | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | C |  | ctrl | 2030 | 0.8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | C |  | ctrl | 2050 | 0.8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | C |  | lower | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Space requirement [1000 m2/MW_e] | Space requirement |  | 1000 m2/MW_e |  | C |  | upper | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2015 | 20
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2020 | 20
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2030 | 20
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | ctrl | 2050 | 20
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | lower | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  |  | upper | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2015 | 0.9
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2020 | 0.9
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [E, F] |  | lower | 2020 | 0.85
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [E, F] |  | upper | 2020 | 0.95
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2030 | 0.9
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2050 | 0.9
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [E, F] |  | lower | 2050 | 0.85
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_e] | Nominal investment | equipment | MEUR/MW_e | 2015 | [E, F] |  | upper | 2050 | 0.95
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2015 | 0.1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2020 | 0.1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [E, F] |  | lower | 2020 | 0.15
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [E, F] |  | upper | 2020 | 0.05
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2030 | 0.1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2050 | 0.1
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [E, F] |  | lower | 2050 | 0.15
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_e] | Nominal investment | installation | MEUR/MW_e | 2015 | [E, F] |  | upper | 2050 | 0.05
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | G |  | ctrl | 2015 | 100000
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | G |  | ctrl | 2020 | 95000
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | G |  | lower | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | G |  | upper | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | G |  | ctrl | 2030 | 90000
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | G |  | ctrl | 2050 | 85000
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | G |  | lower | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_e/y] | Fixed O&M | *total | EUR/MW_e/y | 2015 | G |  | upper | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2015 | 4
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2020 | 3.8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, F] |  | lower | 2020 | 3
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, F] |  | upper | 2020 | 6
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2030 | 3.61
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2050 | 3.4295
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, F] |  | lower | 2050 | 3
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, F] |  | upper | 2050 | 6
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2015
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | lower | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | upper | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2030
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | ctrl | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | lower | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2015 |  |  | upper | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D |  | ctrl | 2015
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D |  | ctrl | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D |  | lower | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D |  | upper | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D |  | ctrl | 2030
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D |  | ctrl | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D |  | lower | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | D |  | upper | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D |  | ctrl | 2015
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D |  | ctrl | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D |  | lower | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D |  | upper | 2020
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D |  | ctrl | 2030
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D |  | ctrl | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D |  | lower | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | D |  | upper | 2050
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/unit/y] | Fixed O&M | *total | EUR/unit/y | 2015 | [E, F] |  | ctrl | 2015 | 540
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/unit/y] | Fixed O&M | *total | EUR/unit/y | 2015 | [E, F] |  | ctrl | 2020 | 540
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/unit/y] | Fixed O&M | *total | EUR/unit/y | 2015 | [E, F] |  | lower | 2020 | 350
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/unit/y] | Fixed O&M | *total | EUR/unit/y | 2015 | [E, F] |  | upper | 2020 | 700
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/unit/y] | Fixed O&M | *total | EUR/unit/y | 2015 | [E, F] |  | ctrl | 2030 | 540
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/unit/y] | Fixed O&M | *total | EUR/unit/y | 2015 | [E, F] |  | ctrl | 2050 | 540
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/unit/y] | Fixed O&M | *total | EUR/unit/y | 2015 | [E, F] |  | lower | 2050 | 350
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Fixed O&M (*total) [2015-EUR/unit/y] | Fixed O&M | *total | EUR/unit/y | 2015 | [E, F] |  | upper | 2050 | 700
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Hub height [m] | Hub height |  | m |  | H |  | ctrl | 2015 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Hub height [m] | Hub height |  | m |  | H |  | ctrl | 2020 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Hub height [m] | Hub height |  | m |  | H |  | lower | 2020 | 14
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Hub height [m] | Hub height |  | m |  | H |  | upper | 2020 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Hub height [m] | Hub height |  | m |  | H |  | ctrl | 2030 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Hub height [m] | Hub height |  | m |  | H |  | ctrl | 2050 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Hub height [m] | Hub height |  | m |  | H |  | lower | 2050 | 14
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Hub height [m] | Hub height |  | m |  | H |  | upper | 2050 | 18
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | H |  | ctrl | 2015 | 8
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | H |  | ctrl | 2020 | 11
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | H |  | lower | 2020 | 4
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | H |  | upper | 2020 | 14
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | H |  | ctrl | 2030 | 12
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | H |  | ctrl | 2050 | 14
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | H |  | lower | 2050 | 4
20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Technology-specific data | Rotor diameter [m] | Rotor diameter |  | m |  | H |  | upper | 2050 | 14
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  |  | 4 | ctrl | 2015 | 1500
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  |  | 4 | ctrl | 2020 | 2500
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  |  | 4 | ctrl | 2030 | 3500
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Average annual full-load hours [MWh_e/MW_e] | Average annual full-load hours |  | MWh_e/MW_e |  |  | 4 | ctrl | 2050 | 4500
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Availability [] | Availability |  | [] |  |  | 4 | ctrl | 2015 | 0.9
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Availability [] | Availability |  | [] |  |  | 4 | ctrl | 2020 | 0.95
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Availability [] | Availability |  | [] |  |  | 4 | ctrl | 2030 | 0.97
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Availability [] | Availability |  | [] |  |  | 4 | ctrl | 2050 | 0.98
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 4 | ctrl | 2015
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 4 | ctrl | 2020 | 3.5
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 4 | ctrl | 2030 | 3.5
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | C | 4 | ctrl | 2050 | 3.5
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | [1, 1, 4, 4] | ctrl | 2015
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | [1, 1, 4, 4] | ctrl | 2020
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | [1, 1, 4, 4] | ctrl | 2030
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Generating capacity for one unit [MW_e] | Generating capacity for one unit |  | MW_e |  |  | [1, 1, 4, 4] | ctrl | 2050
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Length of installation of one power plant [km] | Length of installation of one power plant |  | km |  |  | [1, 1, 4, 4] | ctrl | 2015
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Length of installation of one power plant [km] | Length of installation of one power plant |  | km |  |  | [1, 1, 4, 4] | ctrl | 2020
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Length of installation of one power plant [km] | Length of installation of one power plant |  | km |  |  | [1, 1, 4, 4] | ctrl | 2030
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Technology-specific data | Length of installation of one power plant [km] | Length of installation of one power plant |  | km |  |  | [1, 1, 4, 4] | ctrl | 2050
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 4 | ctrl | 2015 | 10
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 4 | ctrl | 2020 | 20
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 4 | ctrl | 2030 | 25
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 4 | ctrl | 2050 | 30
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [A, B] | [2, 2, 2, 3] | ctrl | 2015
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [A, B] | [2, 2, 2, 3] | ctrl | 2020
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [A, B] | [2, 2, 2, 3] | ctrl | 2030
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [A, B] | [2, 2, 2, 3] | ctrl | 2050 | 1.6
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2011 |  | 4 | ctrl | 2015 | 20
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2011 |  | 4 | ctrl | 2020 | 15
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2011 |  | 4 | ctrl | 2030 | 10
23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Variable O&M (*total) [2011-EUR/MWh_e] | Variable O&M | *total | EUR/MWh_e | 2011 |  | 4 | ctrl | 2050 | 7
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2020 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2025 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | lower | 2025 | 0.3
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2030 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2040 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2050 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | lower | 2050 | 0.3
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2020 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2025 | 0.3
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2025 | 1.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2030 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2040 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2050 | 0.2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2050 | 1.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2020 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | lower | 2025 | 0.7
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | upper | 2025 | 2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2030 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2040 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | lower | 2050 | 0.7
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | upper | 2050 | 2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 2.9
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 2.95
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 2.75
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 3.35
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 3
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 3.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 3.15
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 2.85
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 3.55
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2020 | 2.55
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2025 | 2.6
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | lower | 2025 | 2.4
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | upper | 2025 | 3
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2030 | 2.65
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2040 | 2.75
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2050 | 2.8
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | lower | 2050 | 2.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | upper | 2050 | 3.2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 1.0703
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 1.0703
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.71354
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 1.4271
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.99895
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.99895
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.99895
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.71354
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 1.4271
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2020 | 0.028542
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2025 | 0.028542
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | lower | 2025 | 0.019028
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | upper | 2025 | 0.19028
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2030 | 0.026639
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2040 | 0.026639
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2050 | 0.026639
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | lower | 2050 | 0.019028
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | upper | 2050 | 0.19028
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.25687
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.25687
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.17125
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.19028
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.23975
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.23975
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.23975
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.17125
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.19028
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2020 | 2.69
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2025 | 2.69
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | lower | 2025 | 2.17
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | upper | 2025 | 3.17
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2030 | 2.69
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2040 | 2.69
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2050 | 2.69
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | lower | 2050 | 2.17
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | upper | 2050 | 3.17
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2020 | 2000
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2025 | 2000
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | lower | 2025 | 1000
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | upper | 2025 | 3000
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2030 | 2000
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2040 | 2000
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2050 | 2000
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | lower | 2050 | 1000
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | upper | 2050 | 5000
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2020 | 1.4271
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2025 | 1.4271
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2025 | 0.95139
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2025 | 1.9028
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2030 | 1.3319
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2040 | 1.3319
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2050 | 1.3319
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2050 | 0.95139
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2050 | 1.9028
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2020 | 10
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2025 | 10
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | lower | 2025 | 5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | upper | 2025 | 20
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2030 | 10
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2040 | 10
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2050 | 10
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | lower | 2050 | 2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | upper | 2050 | 20
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2020 | 2.69
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2025 | 2.69
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2025 | 2.17
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2025 | 3.17
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2030 | 2.69
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2040 | 2.69
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2050 | 2.69
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2050 | 2.17
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2050 | 3.17
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2020 | 0.7
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2025 | 0.7
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2030 | 0.6
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2040 | 0.6
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2050 | 0.6
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | lower | 2050 | 0.4
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2020 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2025 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2025 | 1.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2025 | 5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2030 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2040 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2050 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2050 | 1.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2050 | 5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2020 | 0.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2025 | 0.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | lower | 2025 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | upper | 2025 | 1.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2030 | 0.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2040 | 0.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2050 | 0.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | lower | 2050 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | upper | 2050 | 1.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 3.4
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 3.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 3.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 3.7
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 3.6
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 3.65
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 3.7
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 3.3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 3.8
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2020 | 3.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2025 | 3.15
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | lower | 2025 | 2.9
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | upper | 2025 | 3.3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2030 | 3.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2040 | 3.3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2050 | 3.4
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | lower | 2050 | 3
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | upper | 2050 | 3.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.76111
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.76111
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.60889
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 1.1417
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.685
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.685
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.685
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.53278
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 1.1417
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2020 | 0.019028
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2025 | 0.019028
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | lower | 2025 | 0.015222
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | upper | 2025 | 0.14271
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2030 | 0.017125
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2040 | 0.017125
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2050 | 0.017125
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | lower | 2050 | 0.013319
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | upper | 2050 | 0.14271
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.17125
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.17125
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.137
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.14271
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.15412
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.15412
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.15412
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.11987
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.14271
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2020 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2025 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | lower | 2025 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | upper | 2025 | 3.69
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2030 | 2.51
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2040 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2050 | 2.67
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | lower | 2050 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | upper | 2050 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2020 | 2000
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2025 | 2000
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | lower | 2025 | 1000
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | upper | 2025 | 3000
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2030 | 2000
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2040 | 2000
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2050 | 2000
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | lower | 2050 | 1000
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | upper | 2050 | 5000
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2020 | 0.95139
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2025 | 0.95139
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2025 | 0.76111
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2025 | 1.4271
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2030 | 0.85625
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2040 | 0.85625
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2050 | 0.85625
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2050 | 0.66597
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2050 | 1.4271
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2020 | 10
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2025 | 10
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | lower | 2025 | 5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | upper | 2025 | 20
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2030 | 10
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2040 | 10
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2050 | 10
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | lower | 2050 | 2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | upper | 2050 | 20
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2020 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2025 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2025 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2025 | 3.69
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2030 | 2.51
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2040 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2050 | 2.67
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2050 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2050 | 2.19
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2020 | 0.7
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2025 | 0.7
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2030 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2040 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | ctrl | 2050 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | lower | 2050 | 0.4
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [F, G] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2020 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2025 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2025 | 5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2025 | 20
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2030 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2040 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2050 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2050 | 5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2050 | 20
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2020 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2025 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | lower | 2025 | 0.4
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | upper | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2030 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2040 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | ctrl | 2050 | 0.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | lower | 2050 | 0.4
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | Q | [15, 18] | upper | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 3.8
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 3.8
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 3.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 4
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 3.85
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 3.9
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 3.9
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 3.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 4.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2020 | 3.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2025 | 3.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | lower | 2025 | 3.3
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | upper | 2025 | 3.7
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2030 | 3.55
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2040 | 3.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | ctrl | 2050 | 3.6
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | lower | 2050 | 3.3
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, C] | [1, 14, 15] | upper | 2050 | 3.8
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.685
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.685
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.53278
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.91333
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.60889
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.60889
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.60889
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.53278
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.91333
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2020 | 0.017125
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2025 | 0.017125
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | lower | 2025 | 0.013319
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | upper | 2025 | 0.11417
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2030 | 0.015222
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2040 | 0.015222
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | ctrl | 2050 | 0.015222
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | lower | 2050 | 0.013319
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | K | [1, 14, 15] | upper | 2050 | 0.11417
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.15412
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.15412
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.11987
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.11417
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.137
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.137
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.137
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.11987
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.11417
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [E, N] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2020 | 1.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2025 | 1.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | lower | 2025 | 1.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | upper | 2025 | 2.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2030 | 1.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2040 | 1.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2050 | 1.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | lower | 2050 | 1.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | M | [1, 14, 15] | upper | 2050 | 2.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2020 | 2000
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2025 | 2000
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | lower | 2025 | 1000
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | upper | 2025 | 3000
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2030 | 2000
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2040 | 2000
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | ctrl | 2050 | 2000
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | lower | 2050 | 1000
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | M | [1, 14, 15] | upper | 2050 | 5000
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2020 | 0.85625
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2025 | 0.85625
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2025 | 0.66597
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2025 | 1.1417
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2030 | 0.76111
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2040 | 0.76111
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2050 | 0.76111
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | lower | 2050 | 0.66597
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | upper | 2050 | 1.1417
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2020 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2025 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | lower | 2025 | 5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | upper | 2025 | 20
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2030 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2040 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | ctrl | 2050 | 10
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | lower | 2050 | 2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | O | 15 | upper | 2050 | 20
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2020 | 1.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2025 | 1.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2025 | 2.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2030 | 1.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2040 | 1.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2050 | 1.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2050 | 2.69
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [H, I] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [H, J] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | H | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2020 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2025 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | lower | 2025 | 0.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2030 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2040 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2050 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | lower | 2050 | 0.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2020 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2025 | 0.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2025 | 1.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2030 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2040 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2050 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2050 | 1.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | lower | 2025 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | upper | 2025 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | lower | 2050 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | upper | 2050 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2020 | 4.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2025 | 4.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | lower | 2025 | 4.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | upper | 2025 | 4.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2030 | 4.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2040 | 4.4
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2050 | 4.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | lower | 2050 | 4.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | upper | 2050 | 4.8
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 4
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 4.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 4
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 4.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 4.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 4.3
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 4.4
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 4
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 4.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.9276
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.9276
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.71354
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 1.4271
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.85625
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.85625
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.85625
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.71354
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 1.4271
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2020 | 0.024736
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2025 | 0.024736
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | lower | 2025 | 0.019028
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | upper | 2025 | 0.19028
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2030 | 0.022833
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2040 | 0.022833
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2050 | 0.022833
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | lower | 2050 | 0.019028
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | upper | 2050 | 0.19028
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.22262
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.22262
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.17125
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.19028
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.2055
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.2055
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.2055
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.17125
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.19028
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2020 | 2.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2025 | 2.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | lower | 2025 | 1.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | upper | 2025 | 2.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2030 | 2.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2040 | 3.09
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2050 | 3.17
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | lower | 2050 | 2.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | upper | 2050 | 3.17
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2020 | 2000
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2025 | 2000
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | lower | 2025 | 1000
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | upper | 2025 | 3000
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2030 | 2000
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2040 | 2000
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2050 | 2000
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | lower | 2050 | 1000
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | upper | 2050 | 5000
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 1.2368
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2025 | 1.2368
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | lower | 2025 | 0.95139
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | upper | 2025 | 1.9028
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2030 | 1.1417
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2040 | 1.1417
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2050 | 1.1417
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | lower | 2050 | 0.95139
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | upper | 2050 | 1.9028
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2020 | 10
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2025 | 10
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | lower | 2025 | 5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | upper | 2025 | 20
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2030 | 10
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2040 | 10
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2050 | 10
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | lower | 2050 | 2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | upper | 2050 | 20
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2020 | 2.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2025 | 2.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2025 | 1.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2025 | 2.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2030 | 2.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2040 | 3.09
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2050 | 3.17
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2050 | 2.69
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2050 | 3.17
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2020 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2025 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | lower | 2025 | 0.3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2030 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2040 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2050 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | lower | 2050 | 0.3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2020 | 3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2025 | 3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2025 | 1.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2025 | 5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2030 | 3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2040 | 3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2050 | 3
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2050 | 1.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2050 | 5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2020 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2025 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | lower | 2025 | 0.03
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | upper | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2030 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2040 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2050 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | lower | 2050 | 0.03
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | upper | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2020 | 4.6
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2025 | 4.7
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | lower | 2025 | 4.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | upper | 2025 | 4.9
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2030 | 4.8
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2040 | 4.9
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2050 | 5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | lower | 2050 | 4.6
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | upper | 2050 | 5.2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 4.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 4.6
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 4.4
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 4.8
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 4.7
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 4.8
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 4.9
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 4.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 5.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.685
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.685
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.53278
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.91333
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.60889
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.60889
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.60889
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.53278
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.91333
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2020 | 0.017125
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2025 | 0.017125
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | lower | 2025 | 0.013319
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | upper | 2025 | 0.11417
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2030 | 0.015222
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2040 | 0.015222
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2050 | 0.015222
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | lower | 2050 | 0.013319
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | upper | 2050 | 0.11417
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.15412
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.15412
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.11987
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.11417
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.137
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.137
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.137
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.11987
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.11417
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2020 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2025 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | lower | 2025 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | upper | 2025 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2030 | 2.51
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2040 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2050 | 2.67
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | lower | 2050 | 2.17
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | upper | 2050 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2020 | 2000
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2025 | 2000
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | lower | 2025 | 1000
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | upper | 2025 | 3000
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2030 | 2000
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2040 | 2000
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2050 | 2000
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | lower | 2050 | 1000
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | upper | 2050 | 5000
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 0.85625
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2025 | 0.85625
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | lower | 2025 | 0.66597
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | upper | 2025 | 1.1417
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2030 | 0.76111
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2040 | 0.76111
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2050 | 0.76111
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | lower | 2050 | 0.66597
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | upper | 2050 | 1.1417
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2020 | 10
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2025 | 10
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | lower | 2025 | 5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | upper | 2025 | 20
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2030 | 10
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2040 | 10
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2050 | 10
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | lower | 2050 | 2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | upper | 2050 | 20
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2020 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2025 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2025 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2025 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2030 | 2.51
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2040 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2050 | 2.67
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2050 | 2.17
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2050 | 2.19
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2020 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2025 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | lower | 2025 | 0.3
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2030 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2040 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2050 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | lower | 2050 | 0.3
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2020 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2025 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2025 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2025 | 20
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2030 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2040 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2050 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2050 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2050 | 20
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2020 | 0.03
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2025 | 0.03
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | lower | 2025 | 0.02
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | upper | 2025 | 0.06
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2030 | 0.03
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2040 | 0.03
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | ctrl | 2050 | 0.03
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | lower | 2050 | 0.02
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  | [15, 18] | upper | 2050 | 0.06
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2020 | 5.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2025 | 5.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | lower | 2025 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | upper | 2025 | 5.3
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2030 | 5.3
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2040 | 5.4
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | ctrl | 2050 | 5.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | lower | 2050 | 5.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, A1, C, D] | [1, 14, 15] | upper | 2050 | 5.7
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2020 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2025 | 5.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2025 | 4.9
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2025 | 5.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2030 | 5.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2040 | 5.3
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | ctrl | 2050 | 5.4
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | lower | 2050 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, A1, B, D] | [1, 14, 15] | upper | 2050 | 5.6
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.53278
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.53278
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.38055
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.76111
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.45666
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.45666
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.45666
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.38055
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.76111
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2020 | 0.013319
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2025 | 0.013319
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | lower | 2025 | 0.0095139
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | upper | 2025 | 0.095139
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2030 | 0.011417
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2040 | 0.011417
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2050 | 0.011417
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | lower | 2050 | 0.0095139
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | upper | 2050 | 0.095139
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.11987
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.11987
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.085625
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.095139
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.10275
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.10275
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.10275
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.085625
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.095139
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | [D, M] | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2020 | 1.69
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2025 | 1.69
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | lower | 2025 | 1.19
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | upper | 2025 | 2.19
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2030 | 2.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2040 | 2.09
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2050 | 1.69
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | lower | 2050 | 1.69
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | upper | 2050 | 2.67
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2020 | 2000
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2025 | 2000
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | lower | 2025 | 1000
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | upper | 2025 | 3000
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2030 | 2000
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2040 | 2000
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2050 | 2000
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | lower | 2050 | 1000
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | upper | 2050 | 5000
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 0.66597
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2025 | 0.66597
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | lower | 2025 | 0.47569
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | upper | 2025 | 0.95139
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2030 | 0.57083
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2040 | 0.57083
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2050 | 0.57083
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | lower | 2050 | 0.47569
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | upper | 2050 | 0.95139
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2020 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2025 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | lower | 2025 | 5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | upper | 2025 | 20
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2030 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2040 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2050 | 10
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | lower | 2050 | 2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | upper | 2050 | 20
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2020 | 1.69
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2025 | 1.69
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2025 | 1.19
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2025 | 2.19
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2030 | 2.01
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2040 | 2.09
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2050 | 1.69
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2050 | 1.69
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2050 | 2.67
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | lower | 2025 | 0.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | lower | 2050 | 0.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | upper | 2025 | 0.2
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | upper | 2050 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2020 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2025 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | lower | 2025 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | upper | 2025 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2030 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2040 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | ctrl | 2050 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | lower | 2050 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | D | [1, 14, 15] | upper | 2050 | 0.01
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | lower | 2025 | 0.7
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | upper | 2025 | 1.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | [E, F] | [9, 14, 15] | upper | 2050 | 1.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2020 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2025 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2025 | 10
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2025 | 50
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2030 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2040 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2050 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2050 | 10
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2050 | 100
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2020 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2025 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2025 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2025 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2030 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2040 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | ctrl | 2050 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | lower | 2050 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | [1, 14, 15] | upper | 2050 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | O | [15, 18] | ctrl | 2020 | 0.03
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | O | [15, 18] | ctrl | 2025 | 0.03
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | O | [15, 18] | lower | 2025 | 0.02
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | O | [15, 18] | upper | 2025 | 0.06
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | O | [15, 18] | ctrl | 2030 | 0.03
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | O | [15, 18] | ctrl | 2040 | 0.03
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | O | [15, 18] | ctrl | 2050 | 0.03
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | O | [15, 18] | lower | 2050 | 0.02
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | O | [15, 18] | upper | 2050 | 0.06
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2020 | 25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2025 | 25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2025 | 15
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2025 | 40
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2030 | 25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2040 | 25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | ctrl | 2050 | 25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | lower | 2050 | 15
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | [1, 9, 10, 14, 15] | upper | 2050 | 40
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, C, D] | [1, 14, 15] | ctrl | 2020 | 3.7
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, C, D] | [1, 14, 15] | ctrl | 2025 | 3.7
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, C, D] | [1, 14, 15] | lower | 2025 | 3.6
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, C, D] | [1, 14, 15] | upper | 2025 | 3.8
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, C, D] | [1, 14, 15] | ctrl | 2030 | 3.7
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, C, D] | [1, 14, 15] | ctrl | 2040 | 3.8
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, C, D] | [1, 14, 15] | ctrl | 2050 | 3.8
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, C, D] | [1, 14, 15] | lower | 2050 | 3.7
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | [A, C, D] | [1, 14, 15] | upper | 2050 | 3.9
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, D] | [1, 14, 15] | ctrl | 2020 | 3.4
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, D] | [1, 14, 15] | ctrl | 2025 | 3.4
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, D] | [1, 14, 15] | lower | 2025 | 3.3
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, D] | [1, 14, 15] | upper | 2025 | 3.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, D] | [1, 14, 15] | ctrl | 2030 | 3.4
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, D] | [1, 14, 15] | ctrl | 2040 | 3.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, D] | [1, 14, 15] | ctrl | 2050 | 3.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, D] | [1, 14, 15] | lower | 2050 | 3.4
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | [A, B, D] | [1, 14, 15] | upper | 2050 | 3.6
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.40434
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.40434
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.2426
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.85
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.32347
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.32347
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.32347
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.2426
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.85
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2020 | 0.0047569
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2025 | 0.0045257
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | lower | 2025 | 0.0027154
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | upper | 2025 | 0.095139
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2030 | 0.0036205
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2040 | 0.0036205
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | ctrl | 2050 | 0.0036205
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | lower | 2050 | 0.0027154
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (grid connection) [2015-MEUR/MW_e] | Nominal investment | grid connection | MEUR/MW_e | 2015 | J | [1, 14, 15] | upper | 2050 | 0.095139
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2020 | 0.071354
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2025 | 0.071354
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2025 | 0.042812
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2025 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2030 | 0.057083
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2040 | 0.057083
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | ctrl | 2050 | 0.057083
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | lower | 2050 | 0.042812
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 | A | [1, 14, 15] | upper | 2050 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2020 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M | [1, 14, 15] | lower | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M | [1, 14, 15] | upper | 2025 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2030 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2040 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M | [1, 14, 15] | ctrl | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M | [1, 14, 15] | lower | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M | [1, 14, 15] | upper | 2050 | 0
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2020 | 1.19
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2025 | 1.19
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | lower | 2025 | 1.19
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | upper | 2025 | 1.69
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2030 | 1.51
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2040 | 1.59
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | ctrl | 2050 | 1.67
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | lower | 2050 | 1.47
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | L | [1, 14, 15] | upper | 2050 | 1.19
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2020 | 4000
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2025 | 4000
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | lower | 2025 | 2000
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | upper | 2025 | 5000
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2030 | 4000
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2040 | 4000
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | ctrl | 2050 | 4000
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | lower | 2050 | 2000
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | L | [1, 14, 15] | upper | 2050 | 5000
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 0.47569
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2025 | 0.47569
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | lower | 2025 | 0.28542
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | upper | 2025 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2030 | 0.38055
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2040 | 0.38055
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2050 | 0.38055
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | lower | 2050 | 0.28542
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | upper | 2050 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2020 | 10
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2025 | 10
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | lower | 2025 | 5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | upper | 2025 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2030 | 10
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2040 | 10
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | ctrl | 2050 | 10
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | lower | 2050 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Startup cost [2015-EUR/MW_h/startup] | Startup cost |  | EUR/MW_h/startup | 2015 | N | 15 | upper | 2050 | 20
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2020 | 1.19
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2025 | 1.19
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2025 | 1.19
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2025 | 1.69
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2030 | 1.51
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2040 | 1.59
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | ctrl | 2050 | 1.67
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | lower | 2050 | 1.47
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  | [1, 14, 15] | upper | 2050 | 1.19
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2020 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2025 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | lower | 2025 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | upper | 2025 | 3
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2030 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2040 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | ctrl | 2050 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | lower | 2050 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | [G, H] | [9, 14, 15] | upper | 2050 | 2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2020 | 0.25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2025 | 0.25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2030 | 0.25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2040 | 0.25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | ctrl | 2050 | 0.25
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | [G, I] | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | lower | 2025 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | upper | 2025 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | lower | 2050 | 0.05
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | G | [1, 9, 14, 15] | upper | 2050 | 0.5
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2020 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2025 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | upper | 2025 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2030 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2040 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | ctrl | 2050 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | G | [1, 9, 14, 15] | upper | 2050 | 1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2020 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2025 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | lower | 2025 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | upper | 2025 | 0.3
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2030 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2040 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | ctrl | 2050 | 0.2
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | lower | 2050 | 0.1
40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | G | [9, 14, 15] | upper | 2050 | 0.3
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2015 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2020 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2020 | 0.3
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2020 | 0.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2030 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | ctrl | 2050 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | lower | 2050 | 0.3
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  |  | upper | 2050 | 0.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | 3 | ctrl | 2015 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | 3 | ctrl | 2020 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | 3 | lower | 2020 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | 3 | upper | 2020 | 0.03
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | 3 | ctrl | 2030 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | 3 | ctrl | 2050 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | 3 | lower | 2050 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | E | 3 | upper | 2050 | 0.03
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C |  | upper | 2020 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  | C |  | upper | 2050 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, A1] | 13 | ctrl | 2015 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, A1] | 13 | ctrl | 2020 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, A1] | 13 | lower | 2020 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, A1] | 13 | upper | 2020 | 20
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, A1] | 13 | ctrl | 2030 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, A1] | 13 | ctrl | 2050 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, A1] | 13 | lower | 2050 | 12
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [A, A1] | 13 | upper | 2050 | 30
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D |  | upper | 2020 | 1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | D |  | upper | 2050 | 1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2015 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2020 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | lower | 2020 | 0.005
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | upper | 2020 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2030 | 0.005
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | ctrl | 2050 | 0.005
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | lower | 2050 | 0.005
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  |  |  | upper | 2050 | 0.01
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 3 | ctrl | 2015 | 25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 3 | ctrl | 2020 | 25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 3 | lower | 2020 | 15
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 3 | upper | 2020 | 30
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 3 | ctrl | 2030 | 25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 3 | ctrl | 2050 | 25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 3 | lower | 2050 | 15
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 3 | upper | 2050 | 30
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | 4 | ctrl | 2015 | 1.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | 4 | ctrl | 2020 | 1.71
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | 4 | lower | 2020 | 1.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | 4 | upper | 2020 | 1.8
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | 4 | ctrl | 2030 | 1.73
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | 4 | ctrl | 2050 | 1.75
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | 4 | lower | 2050 | 1.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | 4 | upper | 2050 | 1.8
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2015
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2020
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | lower | 2020
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | upper | 2020
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2030
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | ctrl | 2050
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | lower | 2050
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  |  |  | upper | 2050
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | upper | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  |  |  | upper | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | 3 | ctrl | 2015 | 50
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | 3 | ctrl | 2020 | 50
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | 3 | lower | 2020 | 30
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | 3 | upper | 2020 | 70
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | 3 | ctrl | 2030 | 50
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | 3 | ctrl | 2050 | 50
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | 3 | lower | 2050 | 30
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | 3 | upper | 2050 | 70
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | 3 | ctrl | 2015 | 50
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | 3 | ctrl | 2020 | 50
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | 3 | lower | 2020 | 30
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | 3 | upper | 2020 | 70
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | 3 | ctrl | 2030 | 50
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | 3 | ctrl | 2050 | 50
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | 3 | lower | 2050 | 30
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | 3 | upper | 2050 | 70
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | E |  | ctrl | 2015 | 0.6
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | E |  | ctrl | 2020 | 0.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | E |  | lower | 2020 | 0.7
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | E |  | upper | 2020 | 2.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | E |  | ctrl | 2030 | 1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | E |  | ctrl | 2050 | 1.2
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | E |  | lower | 2050 | 1.2
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | E |  | upper | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | 3 | ctrl | 2015 | 0.3
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | 3 | ctrl | 2020 | 0.282
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | 3 | lower | 2020 | 0.3
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | 3 | upper | 2020 | 0.4
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | 3 | ctrl | 2030 | 0.2538
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | 3 | ctrl | 2050 | 0.22842
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | 3 | lower | 2050 | 0.2
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | 3 | upper | 2050 | 0.3
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  | 3 | ctrl | 2015 | 2000
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  | 3 | ctrl | 2020 | 2000
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  | 3 | lower | 2020 | 1000
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  | 3 | upper | 2020 | 3000
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  | 3 | ctrl | 2030 | 2000
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  | 3 | ctrl | 2050 | 2000
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  | 3 | lower | 2050 | 1000
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 |  | 3 | upper | 2050 | 3000
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, A1] | 3 | ctrl | 2015 | 0.6
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, A1] | 3 | ctrl | 2020 | 0.564
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, A1] | 3 | lower | 2020 | 0.4
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, A1] | 3 | upper | 2020 | 0.8
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, A1] | 3 | ctrl | 2030 | 0.5076
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, A1] | 3 | ctrl | 2050 | 0.45684
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, A1] | 3 | lower | 2050 | 0.4
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, A1] | 3 | upper | 2050 | 0.8
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2015 | 0.9
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2020 | 0.982
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2020 | 1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2020 | 2.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2030 | 1.2538
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2050 | 1.4284
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2050 | 1.4
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2050 | 0.3
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2015 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2020 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2020 | 0.25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2020 | 2
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2030 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | ctrl | 2050 | 0.5
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | lower | 2050 | 0.25
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  |  | upper | 2050 | 2
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2015 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2020 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2020 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2020 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2030 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | ctrl | 2050 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | lower | 2050 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  |  | upper | 2050 | 0.1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2015
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2020
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2020
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2020
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2030
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | ctrl | 2050
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | lower | 2050
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  |  |  | upper | 2050
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2015
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2020
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2020
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2020
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2030
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | ctrl | 2050
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | lower | 2050
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  |  |  | upper | 2050
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2015 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2020 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2020 | 1
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050 | 0
40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 9 | ctrl | 2015 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 9 | ctrl | 2020 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 9 | lower | 2020 | 0.2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 9 | upper | 2020 | 0.7
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 9 | ctrl | 2030 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 9 | ctrl | 2050 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 9 | lower | 2050 | 0.2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  | F | 9 | upper | 2050 | 0.7
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | L | 1 | ctrl | 2015 | 0.0015
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | L | 1 | ctrl | 2020 | 0.0014
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | L | 1 | lower | 2020 | 0.0013
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | L | 1 | upper | 2020 | 0.002
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | L | 1 | ctrl | 2030 | 0.0012
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | L | 1 | ctrl | 2050 | 0.001
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | L | 1 | lower | 2050 | 0.0008
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | L | 1 | upper | 2050 | 0.0015
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | ctrl | 2015 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | ctrl | 2020 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | lower | 2020 | 0.0008
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | upper | 2020 | 0.02
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | ctrl | 2030 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | ctrl | 2050 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | lower | 2050 | 0.0008
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 3 | upper | 2050 | 0.02
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2015
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2020
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2020 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2020 | 10
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2030
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | ctrl | 2050
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | lower | 2050 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  |  |  | upper | 2050 | 10
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | F | 3 | ctrl | 2015 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | F | 3 | ctrl | 2020 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | F | 3 | lower | 2020 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | F | 3 | upper | 2020 | 0.6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | F | 3 | ctrl | 2030 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | F | 3 | ctrl | 2050 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | F | 3 | lower | 2050 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  | F | 3 | upper | 2050 | 0.6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | E | 2 | ctrl | 2015 | 0.005
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | E | 2 | ctrl | 2020 | 0.005
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | E | 2 | lower | 2020 | 0.003
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | E | 2 | upper | 2020 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | E | 2 | ctrl | 2030 | 0.005
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | E | 2 | ctrl | 2050 | 0.005
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | E | 2 | lower | 2050 | 0.003
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | E | 2 | upper | 2050 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | K | 3 | ctrl | 2015 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | K | 3 | ctrl | 2020 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | K | 3 | lower | 2020 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | K | 3 | upper | 2020
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | K | 3 | ctrl | 2030 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | K | 3 | ctrl | 2050 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | K | 3 | lower | 2050 | 25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  | K | 3 | upper | 2050
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | [1, 3] | ctrl | 2015 | 1.03
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | [1, 3] | ctrl | 2020 | 1.03
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | [1, 3] | lower | 2020 | 0.93
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | [1, 3] | upper | 2020 | 1.05
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | [1, 3] | ctrl | 2030 | 1.04
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | [1, 3] | ctrl | 2050 | 1.04
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | [1, 3] | lower | 2050 | 0.94
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | B | [1, 3] | upper | 2050 | 1.06
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | A | [1, 2, 3] | ctrl | 2015 | 1.05
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | A | [1, 2, 3] | ctrl | 2020 | 1.05
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | A | [1, 2, 3] | lower | 2020 | 0.95
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | A | [1, 2, 3] | upper | 2020 | 1.07
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | A | [1, 2, 3] | ctrl | 2030 | 1.06
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | A | [1, 2, 3] | ctrl | 2050 | 1.06
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | A | [1, 2, 3] | lower | 2050 | 0.96
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Energy/technical data | Heat efficiency (net, name plate) [] | Heat efficiency | net, name plate | [] |  | A | [1, 2, 3] | upper | 2050 | 1.08
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 7 | ctrl | 2015 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 7 | ctrl | 2020 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 7 | lower | 2020
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 7 | upper | 2020
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 7 | ctrl | 2030 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 7 | ctrl | 2050 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 7 | lower | 2050
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  | I | 7 | upper | 2050
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [1, 2] | ctrl | 2015 | 10
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [1, 2] | ctrl | 2020 | 9
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [1, 2] | lower | 2020 | 8
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [1, 2] | upper | 2020 | 60
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [1, 2] | ctrl | 2030 | 7
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [1, 2] | ctrl | 2050 | 6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [1, 2] | lower | 2050 | 5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  | [1, 2] | upper | 2050 | 30
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | H | 1 | ctrl | 2015 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | H | 1 | ctrl | 2020 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | H | 1 | lower | 2020 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | H | 1 | upper | 2020 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | H | 1 | ctrl | 2030 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | H | 1 | ctrl | 2050 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | H | 1 | lower | 2050 | 0
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Environment | SO2 [g/GJ_i] | SO2 |  | g/GJ_i |  | H | 1 | upper | 2050 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 3] | ctrl | 2015 | 0.04
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 3] | ctrl | 2020 | 0.04
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 3] | lower | 2020 | 0.025
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 3] | upper | 2020 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 3] | ctrl | 2030 | 0.03
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 3] | ctrl | 2050 | 0.03
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 3] | lower | 2050 | 0.025
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 3] | upper | 2050 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 3] | ctrl | 2015 | 0.02
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 3] | ctrl | 2020 | 0.02
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 3] | lower | 2020 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 3] | upper | 2020 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 3] | ctrl | 2030 | 0.02
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 3] | ctrl | 2050 | 0.02
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 3] | lower | 2050 | 0.01
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 3] | upper | 2050 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | L |  | ctrl | 2015 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | L |  | ctrl | 2020 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | L |  | lower | 2020 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | L |  | upper | 2020 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | L |  | ctrl | 2030 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | L |  | ctrl | 2050 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | L |  | lower | 2050 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | L |  | upper | 2050 | 0.2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | [8, 9] | ctrl | 2015 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | [8, 9] | ctrl | 2020 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | [8, 9] | lower | 2020 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | [8, 9] | upper | 2020 | 2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | [8, 9] | ctrl | 2030 | 0.9
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | [8, 9] | ctrl | 2050 | 0.9
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | [8, 9] | lower | 2050 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 |  | [8, 9] | upper | 2050 | 2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2015 | 2000
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2020 | 1950
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | lower | 2020 | 1000
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | upper | 2020 | 2500
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2030 | 1900
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | ctrl | 2050 | 1700
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | lower | 2050 | 1000
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | F |  | upper | 2050 | 2500
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | J | [2, 3] | ctrl | 2015 | 0.06
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | J | [2, 3] | ctrl | 2020 | 0.06
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | J | [2, 3] | lower | 2020 | 0.035
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | J | [2, 3] | upper | 2020 | 0.25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | J | [2, 3] | ctrl | 2030 | 0.05
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | J | [2, 3] | ctrl | 2050 | 0.05
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | J | [2, 3] | lower | 2050 | 0.035
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | J | [2, 3] | upper | 2050 | 0.25
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2015 | 1.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2020 | 1.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2020 | 0.6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2020 | 2.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2030 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | ctrl | 2050 | 1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | lower | 2050 | 0.6
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 |  |  | upper | 2050 | 2.2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | D | 9 | ctrl | 2015 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | D | 9 | ctrl | 2020 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | D | 9 | lower | 2020 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | D | 9 | upper | 2020 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | D | 9 | ctrl | 2030 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | D | 9 | ctrl | 2050 | 0.4
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | D | 9 | lower | 2050 | 0.3
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  | D | 9 | upper | 2050 | 0.5
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 9 | ctrl | 2015 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 9 | ctrl | 2020 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 9 | lower | 2020 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 9 | upper | 2020 | 0.2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 9 | ctrl | 2030 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 9 | ctrl | 2050 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 9 | lower | 2050 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  |  | 9 | upper | 2050 | 0.2
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C |  | ctrl | 2015
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C |  | ctrl | 2020
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C |  | lower | 2020
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C |  | upper | 2020
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C |  | ctrl | 2030
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C |  | ctrl | 2050
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C |  | lower | 2050
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | C |  | upper | 2050
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C |  | ctrl | 2015
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C |  | ctrl | 2020
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C |  | lower | 2020
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C |  | upper | 2020
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C |  | ctrl | 2030
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C |  | ctrl | 2050
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C |  | lower | 2050
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | C |  | upper | 2050
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | D | 9 | ctrl | 2015 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | D | 9 | ctrl | 2020 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | D | 9 | lower | 2020 | 0.08
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | D | 9 | upper | 2020 | 0.15
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | D | 9 | ctrl | 2030 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | D | 9 | ctrl | 2050 | 0.1
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | D | 9 | lower | 2050 | 0.08
44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  | D | 9 | upper | 2050 | 0.15
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2020 | 0.041206
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2025 | 0.041375
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2025 | 0.016473
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2025 | 0.074229
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2030 | 0.041538
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2040 | 0.041846
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2050 | 0.041992
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2050 | 0.016473
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2050 | 0.074229
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2020 | 4.5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2025 | 4.5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2025 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2025 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2030 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2040 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2050 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2050 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2050 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2020 | 0.02
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2025 | 0.02
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2025 | 0.01
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2025 | 0.03
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2030 | 0.02
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2040 | 0.02
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2050 | 0.02
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2050 | 0.01
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2050 | 0.03
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 11.4183
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 11.3715
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 19.28
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 4.28
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 11.3269
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 11.2435
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 11.2045
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 19.28
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 4.28
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2020 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2025 | 1
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2025 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2030 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2040 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2050 | 1
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2050 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2025 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2025 | 7
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2050 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2050 | 7
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2020 | 25
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2025 | 25
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2025 | 25
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2025 | 30
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2030 | 30
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2040 | 30
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2050 | 30
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2050 | 25
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2050 | 35
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2020 | 4.6027
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2025 | 4.6719
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2025 | 5.3085
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2025 | 4.059
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2030 | 4.7404
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2040 | 4.8757
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2050 | 4.9424
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2050 | 5.7553
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2050 | 4.3155
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 1.5359
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 1.4907
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 0.86124
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 2.3131
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 1.4455
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 1.4004
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 1.3552
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 0.78295
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 2.1028
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2020 | 0.66597
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2025 | 0.66597
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2025 | 0.47358
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2025 | 0.94844
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2030 | 0.57083
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2040 | 0.57083
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2050 | 0.57083
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2050 | 0.46662
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2050 | 0.93451
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 0.51196
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 0.4969
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 0.29578
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 0.79439
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 0.48184
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 0.46678
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 0.45173
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 0.26889
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 0.72218
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2025 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2025 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2025 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2040 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2050 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2050 | 0
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2020 | 5.6965
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2025 | 5.7127
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2025 | 5.0893
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2025 | 6.0931
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2030 | 6.1276
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2040 | 6.2523
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2050 | 5.8641
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2050 | 5.7517
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2050 | 6.6435
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2020 | 22600
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2025 | 21900
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2025 | 21900
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2025 | 21900
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2030 | 21300
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2040 | 20600
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2050 | 19900
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2050 | 19900
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2050 | 19900
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.7138
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2025 | 2.6536
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2025 | 1.6306
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2025 | 4.0559
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2030 | 2.4982
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2040 | 2.438
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2050 | 2.3777
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2050 | 1.5185
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2050 | 3.7595
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2020 | 5.6965
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2025 | 5.7127
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2025 | 5.0893
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2025 | 6.0931
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2030 | 6.1276
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2040 | 6.2523
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2050 | 5.8641
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2050 | 5.7517
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2050 | 6.6435
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2020 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2030 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2040 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2020 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2025 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2025 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2025 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2030 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2040 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2050 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2050 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2050 | 0.2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2020
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2030
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2040
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2020
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2030
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2040
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2025
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2040
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2020 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2025 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2025 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2025 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2030 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2040 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2050 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2050 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2050 | 1200
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 9.41
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 9.41
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 15.88
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 3.53
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 9.41
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 9.41
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 9.41
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 15.88
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 3.53
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2020 | 2.0103
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2025 | 1.9635
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2025 | 3.3143
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2025 | 0.73674
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2030 | 1.9189
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2040 | 1.8355
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2050 | 1.7965
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2050 | 3.0323
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2050 | 0.67407
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | ctrl | 2020 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | ctrl | 2025 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | lower | 2025 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | upper | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | ctrl | 2030 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | ctrl | 2040 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | ctrl | 2050 | 4
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | lower | 2050 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | upper | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2025 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2025 | 1
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2050 | 3
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2050 | 1
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2020 | 5.68
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2025 | 5.7914
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2025 | 5.7914
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2025 | 5.7914
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2030 | 5.9027
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2040 | 6.1255
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2050 | 6.2369
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2050 | 6.2369
45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2050 | 6.2369
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2020 | 0.065014
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2025 | 0.065126
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2025 | 0.037115
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2025 | 0.092698
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2030 | 0.065233
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2040 | 0.065433
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2050 | 0.065528
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2050 | 0.037115
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2050 | 0.092698
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2020 | 4.5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2025 | 4.5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2025 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2025 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2030 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2040 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2050 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2050 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2050 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2020 | 0.02
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2025 | 0.02
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2025 | 0.01
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2025 | 0.03
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2030 | 0.02
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2040 | 0.02
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2050 | 0.02
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2050 | 0.01
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2050 | 0.03
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 13.1357
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 13.1131
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 22.18
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 4.93
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 13.0916
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 13.0514
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 13.0327
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 22.18
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 4.93
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2020 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2025 | 1
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2025 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2030 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2040 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2050 | 1
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2050 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2025 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2025 | 7
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2050 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2050 | 7
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2020 | 25
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2025 | 25
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2025 | 25
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2025 | 30
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2030 | 30
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2040 | 30
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2050 | 30
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2050 | 25
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2050 | 35
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2020 | 8.4437
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2025 | 8.5533
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2025 | 11.2426
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2025 | 6.504
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2030 | 8.6608
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2040 | 8.8699
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2050 | 8.9715
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2050 | 12.0754
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2050 | 6.774
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 1.9805
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 1.9223
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 1.1384
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 2.8284
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 1.864
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 1.8058
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 1.7475
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 1.0349
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 2.5713
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2020 | 0.24212
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2025 | 0.24139
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2025 | 0.17241
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2025 | 0.34449
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2030 | 0.20631
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2040 | 0.20519
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2050 | 0.20466
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2050 | 0.16949
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2050 | 0.33866
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 0.66017
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 0.64075
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 0.39097
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 0.97138
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 0.62133
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 0.60192
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 0.5825
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 0.35543
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 0.88307
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2025 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2025 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2025 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2040 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2050 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2050 | 0
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2020 | 4.5876
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2025 | 4.5182
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2025 | 4.2909
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2025 | 4.6489
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2030 | 4.5926
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2040 | 4.5594
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2050 | 4.3437
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2050 | 4.3081
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2050 | 4.6244
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2020 | 23900
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2025 | 23200
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2025 | 23200
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2025 | 23200
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2030 | 22500
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2040 | 21800
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2050 | 21100
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2050 | 21100
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2050 | 21100
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.8828
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2025 | 2.8044
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2025 | 1.7018
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2025 | 4.1443
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2030 | 2.6916
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2040 | 2.6129
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2050 | 2.5347
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2050 | 1.5598
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2050 | 3.793
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2020 | 4.5876
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2025 | 4.5182
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2025 | 4.2909
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2025 | 4.6489
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2030 | 4.5926
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2040 | 4.5594
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2050 | 4.3437
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2050 | 4.3081
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2050 | 4.6244
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2020 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2030 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2040 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2020 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2025 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2025 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2025 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2030 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2040 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2050 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2050 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2050 | 0.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2020
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2030
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2040
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2020
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2030
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2040
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2025
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2040
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2020 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2025 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2025 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2025 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2030 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2040 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2050 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2050 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2050 | 2000
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 12.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 12.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2025 | 20.58
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2025 | 4.57
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2030 | 12.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2040 | 12.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2050 | 12.2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | lower | 2050 | 20.58
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | upper | 2050 | 4.57
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2020 | 0.94568
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2025 | 0.92311
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2025 | 1.5612
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2025 | 0.34669
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2030 | 0.90159
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2040 | 0.86143
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | ctrl | 2050 | 0.84267
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | lower | 2050 | 1.4252
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from heat pumps [MW_h] | Heat generation from heat pumps |  | MW_h |  | A | 1 | upper | 2050 | 0.31648
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | ctrl | 2020 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | ctrl | 2025 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | lower | 2025 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | upper | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | ctrl | 2030 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | ctrl | 2040 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | ctrl | 2050 | 4
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | lower | 2050 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of injection wells | Number of injection wells |  |  |  | L | 1 | upper | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2020 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2025 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2025 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2025 | 1
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2030 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2040 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | ctrl | 2050 | 2
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | lower | 2050 | 3
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Number of production wells | Number of production wells |  |  |  | [L, N] | 1 | upper | 2050 | 1
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2020 | 5.05
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2025 | 5.149
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2025 | 5.149
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2025 | 5.149
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2030 | 5.248
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2040 | 5.4461
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | ctrl | 2050 | 5.5451
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | lower | 2050 | 5.5451
45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat pump SCOP (net, annual average) [] | Heat pump SCOP | net, annual average | [] |  | [A, N] |  | upper | 2050 | 5.5451
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2020 | 0.020765
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2025 | 0.020935
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2025 | 0.0082365
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2025 | 0.037009
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2030 | 0.021103
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2040 | 0.021269
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | ctrl | 2050 | 0.021433
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | lower | 2050 | 0.0082365
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Auxiliary Electricity consumption (share of heat gen.) [] | Auxiliary Electricity consumption | share of heat gen. | [] |  | B | [2, 3, 4] | upper | 2050 | 0.037009
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2020 | 4.5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2025 | 4.5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2025 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2025 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2030 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2040 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | ctrl | 2050 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | lower | 2050 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Construction time [years] | Construction time |  | years |  |  | 5 | upper | 2050 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2020 | 0.02
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2025 | 0.02
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2025 | 0.01
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2025 | 0.03
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2030 | 0.02
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2040 | 0.02
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | ctrl | 2050 | 0.02
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | lower | 2050 | 0.01
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Forced outage [] | Forced outage |  | [] |  |  | 5 | upper | 2050 | 0.03
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2020 | 22.6587
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2025 | 22.4747
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2025 | 38.56
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2025 | 8.56
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2030 | 22.2957
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2040 | 22.1215
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | ctrl | 2050 | 21.952
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | lower | 2050 | 38.56
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Generating capacity for one unit [MW_h] | Generating capacity for one unit |  | MW_h |  | [I, A] | [1, 2] | upper | 2050 | 8.56
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2020 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2025 | 1
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2025 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2030 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2040 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | ctrl | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | lower | 2050 | 1
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Planned outage [weeks per year] | Planned outage |  | weeks per year |  |  | 5 | upper | 2050 | 4
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2020 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2025 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2025 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2025 | 7
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2030 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2040 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | ctrl | 2050 | 5
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | lower | 2050 | 3
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Space requirement [1000 m2/MW_h] | Space requirement |  | 1000 m2/MW_h |  | D | 5 | upper | 2050 | 7
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2020 | 25
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2025 | 25
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2025 | 25
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2025 | 30
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2030 | 30
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2040 | 30
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | ctrl | 2050 | 30
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | lower | 2050 | 25
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Technical lifetime [years] | Technical lifetime |  | years |  |  | 5 | upper | 2050 | 35
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2020 | 1.6514
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2025 | 1.6602
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2025 | 1.7235
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2025 | 1.6444
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2030 | 1.6691
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2040 | 1.6779
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | ctrl | 2050 | 1.6867
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | lower | 2050 | 1.7942
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Energy/technical data | Heat efficiency (net, annual average) [] | Heat efficiency | net, annual average | [] |  | AG |  | upper | 2050 | 1.7085
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2020
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2030
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2040
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | ctrl | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | lower | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | CH4 [g/GJ_i] | CH4 |  | g/GJ_i |  |  |  | upper | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2020
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2030
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2040
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | ctrl | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | lower | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | N2O [g/GJ_i] | N2O |  | g/GJ_i |  |  |  | upper | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2020
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2030
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2040
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | ctrl | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | lower | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | NOX [g/GJ_i] | NOX |  | g/GJ_i |  |  |  | upper | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2020
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2030
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2040
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | ctrl | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | lower | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | Particles [g/GJ_i] | Particles |  | g/GJ_i |  |  |  | upper | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2020
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2030
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2040
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | ctrl | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | lower | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Environment | SO2 (degree of desulphuring) [] | SO2 | degree of desulphuring | [] |  |  |  | upper | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 0.77396
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 0.7512
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 0.42665
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 1.1565
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 0.72843
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 0.70567
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 0.68291
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 0.38786
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (equipment) [2015-MEUR/MW_h] | Nominal investment | equipment | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 1.0514
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2020 | 0.23251
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2025 | 0.22395
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2025 | 0.16473
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2025 | 0.32897
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2030 | 0.2152
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2040 | 0.20626
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | ctrl | 2050 | 0.19714
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | lower | 2050 | 0.16473
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (heatpump, installation incl) [2015-MEUR/MW_h] | Nominal investment | heatpump, installation incl | MEUR/MW_h | 2015 | [J, K] |  | upper | 2050 | 0.32897
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2020 | 0.25799
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2025 | 0.2504
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2025 | 0.14652
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2025 | 0.3972
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2030 | 0.24281
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2040 | 0.23522
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | ctrl | 2050 | 0.22764
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | lower | 2050 | 0.1332
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (installation) [2015-MEUR/MW_h] | Nominal investment | installation | MEUR/MW_h | 2015 |  | [2, 4] | upper | 2050 | 0.36109
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2020 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2025 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2025 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2025 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2030 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2040 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | ctrl | 2050 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | lower | 2050 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (electricity cost) [2015-EUR/MWh_h] | Variable O&M | electricity cost | EUR/MWh_h | 2015 | M |  | upper | 2050 | 0
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2020 | 2.0764
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2025 | 2.1069
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2025 | 2.0725
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2025 | 2.0694
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2030 | 2.1375
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2040 | 2.1255
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | ctrl | 2050 | 2.1129
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | lower | 2050 | 2.0301
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (other O&M) [2015-EUR/MWh_h] | Variable O&M | other O&M | EUR/MWh_h | 2015 | F |  | upper | 2050 | 2.027
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2020 | 11100
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2025 | 10800
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2025 | 10800
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2025 | 10800
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2030 | 10500
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2040 | 10100
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | ctrl | 2050 | 9800
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | lower | 2050 | 9800
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Fixed O&M (*total) [2015-EUR/MW_h/y] | Fixed O&M | *total | EUR/MW_h/y | 2015 | [E, J] | [1, 3, 2] | upper | 2050 | 9800
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 1.2645
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2025 | 1.2273
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2025 | 0.7379
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2025 | 1.8827
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2030 | 1.1901
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2040 | 1.1529
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2050 | 1.1157
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | lower | 2050 | 0.68579
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | upper | 2050 | 1.7415
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2020 | 2.0764
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2025 | 2.1069
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2025 | 2.0725
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2025 | 2.0694
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2030 | 2.1375
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2040 | 2.1255
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | ctrl | 2050 | 2.1129
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | lower | 2050 | 2.0301
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Variable O&M (*total) [2015-EUR/MWh_h] | Variable O&M | *total | EUR/MWh_h | 2015 | FJ | 2 | upper | 2050 | 2.027
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2020 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2025 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2030 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2040 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | ctrl | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | lower | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Cold start-up time [hours] | Cold start-up time |  | hours |  |  | 3 | upper | 2050 | 2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2020 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2025 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2025 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2025 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2030 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2040 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | ctrl | 2050 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | lower | 2050 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Minimum load (of full load) [] | Minimum load | of full load | [] |  | H | [2, 5] | upper | 2050 | 0.2
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2020
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2030
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2040
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | ctrl | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | lower | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Primary regulation (of full load, per 30 seconds) [] | Primary regulation | of full load, per 30 seconds | [] |  | H |  | upper | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2020
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2030
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2040
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | ctrl | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | lower | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Secondary regulation (of full load, per minute) [] | Secondary regulation | of full load, per minute | [] |  | H |  | upper | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2020
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2025
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2030
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2040
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | ctrl | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | lower | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Regulation ability | Warm start-up time [hours] | Warm start-up time |  | hours |  |  |  | upper | 2050
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2020 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2025 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2025 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2025 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2030 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2040 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | ctrl | 2050 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | lower | 2050 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Depth of geothermal well [m] | Depth of geothermal well |  | m |  |  | 1 | upper | 2050 | 1200
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2020 | 9.41
45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Technology-specific data | Heat generation from geothermal ressource [MW_h] | Heat generation from geothermal ressource |  | MW_h |  | [I, A, L, N] | 1 | ctrl | 2025 | 9.41